## MM
|  | CIGRE WG A3.29 - Ageing of High Voltage Equipment |  | FALSE | answer | sheet answered ? |  | CIGRE WG A3.06 -Studie spolehlivosti zarizeni vvn a zvn | CIGRE WG A3.29 - Ageing of High Voltage Equipment | CIGRE WG A3.06 - Enquête de fiabilité des équipements haute tension | CIGRE WG A3.06 - Zuverlässigkeitsstudie von Hochspannungs-Geräten | CIGRE WG A3.06 - 高電圧機器の信頼性調査 | CIGRE WG A3.06 - Reliability Study of High Voltage Equipment | CIGRE WG A3.06 - Reliability Study of High Voltage Equipment | CIGRE WG A3.06 - Reliability Study of High Voltage Equipment | CIGRE WG A3.06 - Istraživanje pouzdanosti visokonaponske opreme | CIGRE WG A3.06 - Studio di affidabilità delle apparecchiature per alta tensione | STUDIU DE FIABILITATE A ECHIPAMENTULUI DE INALTA TENSIUNE | Country | 2 digit code | XXX | unknown number
[5 empty] | ALL | type of cards contained in file | [12 empty] | AFGHANISTAN | AF | AFG | 4
[19 empty] | ALBANIA | AL | ALB | 8
|  |  |  | answer ! |  |  |  | Cestina | English | French | German | Japanese | Norwegian | Polski | Spanish | Croatian | Italian | Romanian | ALGERIA | DZ | DZA | 12
|  |  |  | FALSE | 2 | language (column #) | [12 empty] | AMERICAN SAMOA | AS | ASM | 16
|  |  |  | FALSE | 1 | Year | What year are you referring to? | O jakem roce referujete? | What year are you referring to? | A quelle année faites-vous référence ? | Auf welches Jahr beziehen sich Ihre Angaben? | 今回対象の調査年 | Hvilket år er dette for? | Którego roku dotyczy? | ¿A qué año se refiere? | Na koju godinu se odnosi? | A che anno fate riferimento? | La ce an va referiti? | ANDORRA | AD | AND | 20
|  |  |  | English | 3 | sel. Lang (line) |  |  | 2013 |  | Englisch | [7 empty] | ANGOLA | AO | AGO | 24
|  |  |  | 3 | 2013 | begin survey |  |  | 2014 |  | Französisch | [7 empty] | ANGUILLA | AI | AIA | 660
This questionnaire applies to high voltage equipment with rated voltages of 60 kV and above. |  |  |  |  | 2015 | end survey |  |  | 2015 |  | Spanisch | [7 empty] | ANTARCTICA | AQ | ATA | 10
[9 empty] | 2016 | [9 empty] | ANTIGUA AND BARBUDA | AG | ATG | 28
| Organisation Information |  |  |  | #REF! |  | Card number | Cislo dotaznikove karty | Card number | Numero de Carte : | Nummer der Karte | Card Number: | Skjema nr: | Numer Karty: | Ficha número: | Broj kartice: | Card number: | Numarul fisei | ARGENTINA | AR | ARG | 32
[19 empty] | ARMENIA | AM | ARM | 51
Country | [6 empty] | Please answer | Prosim odpovezte | Please answer | répondez, svp | Bitte beantworten | 回答記入 | Vennligst besvar spørmålet | Proszę odpowiedzieć! | responde por favor | Molim odgovorite | Fornire le seguenti informazioni: | Va rugam raspundeti | ARUBA | AW | ABW | 533
Organisation name | [6 empty] | Utility Information | Informace o spolecnosti | Utility Information | Information sur l'exploitant | Informationen zu Ihrem Unternehmen | 会社情報 | Informasjon om everket | Informacja o przedsiębiorstwie energetycznym | Información de la compañía | Informacija o korisniku | Informazioni sul gestore | Informatii despre gestionarul de instalatii | AUSTRALIA | AU | AUS | 36
Short organisation name (max. 7 char.) |  |  |  | FALSE | 40 | Country | Country | Stat | Country | Pays | Staat | 国名 | Land | Kraj | País | Zemlja | Nazione | Tara | AUSTRIA | AT | AUT | 40
Ownership |  |  |  | TRUE | 0 | Utility Name | Utility name | Jmeno spolecnosti | Utility name | Compagnie électrique | Name Ihres Unternehmens | 会社名 | Navn på everket | Nazwa przedsiębiorstwa energetycznego | Nombre | Ime korisnika | Nome gestore | Compania | AZERBAIJAN | AZ | AZE | 31
Organisation type | [6 empty] | Short utility name (max. 7 char.) | Zkratka jmena spolecnosti (max 7 pismen) | Short utility name (max. 7 char.) | Abréviation nom compagnie électr. (max 7 carac.) | Kürzel des Unternehmensnamen (max 7 Buchstaben) | 会社略称 (７文字以内) | Kortversjon (maks. 7 bokstaver) på everk | Skrót nazwy przedsiębiorstwa (max 7 znaków) | Nombre (max 7 c) | Kratica imena korisnika (maks. 7 slova) | Abbrev. gestore (max 7 carat.) | Abrevierea numelui companiei (max 7 carac.) | BAHAMAS | BS | BHS | 44
Mailing address |  |  |  | TRUE | 0 | Utility Name (short form, max 4 char.) | Ownership | Vlastnictvi | Ownership | Appartenance | Besitzverhältnisse | 会社の種類 | Eiere | Rodzaj własności przedsiębiorstwa | Propiedad | Vlasništvo | Proprietà | Apartenenta | BAHRAIN | BH | BHR | 48
Contact name |  |  |  | FALSE | 4 | Ownership | State owned | Statni | State owned | Publique | Staatlich | 官営 | Statlig | Przedsiębiorstwo państwowe | Gubernamental | Državno vlasništvo | Nazionale | In proprietate guvernamentala | BANGLADESH | BD | BGD | 50
Telephone | [6 empty] | Municipal | Vlastnena regionem | Municipal | Municipale | Kommune | 地方自治体 | Annet offentlig | Przedsiębiorstwo miejskie | Municipal | Gradsko vlasništvo | Comunale | Municipala | BARBADOS | BB | BRB | 52
Fax | [6 empty] | Private | Soukroma | Private | Privée | Privat | 民間企業 | Privat | Przedsiębiorstwo prywatne | Privado | Privatno vlasništvo | Privata | Privata | BELARUS | BY | BLR | 112
E-mail | [6 empty] | Other | Jina | Other | Autre | Andere | その他 | Annet | Inne | Otro | Drugo | Altro | Alta | BELGIUM | BE | BEL | 56
[7 empty] | Utility type | Typ splecnosti | Utility type | Type de compagnie | Typ Ihres Unternehmens | 設備の種類 | Type everk | Rodzaj przedsiębiorstwa energetycznego | Tipo de compañía | Tip korisnika | Tipo di gestore | Tip companie | BELIZE | BZ | BLZ | 84
|  |  |  | FALSE | 8 | Utility Type | Distribution only | Pouze distribuce el. energie | Distribution only | Seulement distribution | Nur Energieverteilung | 配電のみ | Kun distribusjon | Wyłącznie dystrybucyjne | Solo distribución | Samo distribucija | Solo distribuzione | Numai distributie | BENIN | BJ | BEN | 204
[7 empty] | Generation only | Pouze vyroba el. energie | Generation only | Seulement production | Nur Energieerzeugung | 発電のみ | Produksjon | Wyłącznie wytwarzanie | Solo generación | Samo proizvodnja | Solo generazione | Numai producere | BERMUDA | BM | BMU | 60
[7 empty] | Generation, transmission and distribution | Vyroba, rozvod/distribuce el. energie | Generation, transmission and distribution | Génération, transmission et distribution | Energieerzeugung, -übertragung und -verteilung | 発電、送変電および配電 | Transmisjon og distribusjon | Wytwarzanie, dystrybucja | Transporte, generatión y distribución | Proizvodnja, distribucija i prijenos | Generazione, trasmissione e distribuzione | Producere, transport si distributie | BHUTAN | BT | BTN | 64
[7 empty] | Industrial | Prumysl | Industrial | Industriel | Industrie | 一般産業 | Industrinett | Przemysłowe | Industrial | Industrija | Industriale | Industriala | BOLIVIA | BO | BOL | 68
[7 empty] | Transmission and distribution | Prenos a distribuce el. energie | Transmission and distribution | Transmission et Distribution | Energieübertragung und -verteilung | 送変電および配電 | Transmisjon og distribusjon | Przesyłowe i dystrybucyjne | Transporte y distribución | Prijenos i distribucija | Trasmissione e distribuzione | Transport si distributie | BOSNIA AND HERZEGOWINA | BA | BIH | 70
[7 empty] | Transmission only | Pouze presnos el. energie | Transmission only | Transmission uniquement | Nur Energieübertragung | 送変電のみ | Kun transmisjon | Wyłącznie przesyłowe | Solo transporte | Samo prijenos | Solo trasmissione | Numai transport | BOTSWANA | BW | BWA | 72
[7 empty] | Manufacturer | Jina | Other | Autre | Andere | その他 | Annet | Inne | Otro | Drugo | Altro | Alta | BOUVET ISLAND | BV | BVT | 74
| Main Menu | [5 empty] | Other | Postovni adresa | Mailing address | Adresse postale | E-Mail Adresse | 住所 | Postadresse | Adres pocztowy | Dirección postal | Poštanska adresa | Indirizzo postale | Adresa postala | BRAZIL | BR | BRA | 76
|  |  |  | TRUE | 0 | Mailing address | Contact name | Jmeno kontaktni osoby | Contact name | Personne à contacter | Ansprechpartner | 連絡先（代表者名） | Kontaktperson | Nazwisko osoby kontaktowej | Contacto | Ime kontakt osobe | Nominativo contatto | Persoana de contact | BRITISH INDIAN OCEAN TERRITORY | IO | IOT | 86
Please, fill the general information card. |  |  |  | TRUE | 0 | Contact name | Telephone | Telefon | Telephone | Téléphone | Telefon | 電話番号 | Telefon | Telefon | Teléfono | Telefon | Telefono | Telefon | BRUNEI DARUSSALAM | BN | BRN | 96
General information about asset management of high voltage equipment |  |  | empty | TRUE | 0 | Telephone | Fax | Fax | Fax | Fax | Fax | Fax | Telefaks | Fax | Fax | Fax | Fax | Fax | BULGARIA | BG | BGR | 100
Please, fill the following cards on equipment ageing.
Ageing card for Gas Circuit Breakers |  |  | empty | TRUE | 0 | Fax | E-mail | E-mail | E-mail | Courrier électronique | E-Mail Adresse | E－MAIL | E-post | E-mail | Correo electrónico | E-mail | E-mail | E-mail | BURKINA FASO | BF | BFA | 854
Ageing card for Oil Circuit Breakers |  |  | empty | TRUE
Ageing card for Airblast Circuit Breakers |  |  | empty | [15 empty] | CAMBODIA | KH | KHM | 116
Ageing card for Disconnectors and Earthing Switches |  |  | empty |  |  |  | an updated "POPULATION CARD" each year at an anniversary date of your choice. | aktualizovany prehled populace zarizeni kazdy rok k datu, který si vyberete | an updated "POPULATION CARD" each year at an anniversary date of your choice. | chaque année à une date anniversaire de votre choix une "carte de POPULATION" à jour, | Bitte senden Sie jedes Jahr ein aktualisiertes "Bestandsblatt" an die CIGRE. | ・毎年Ｃｉｇｒｅ本部にPopulation Card（台数調査票）のデータを更新してデータ提出を御願いします。 | Vær vennlig å send inn et oppdatert "Populasjons-skjema" til CIGRE hvert år | Uaktualnioną KARTĘ POPULACJI prosimy przesłać do CIGRE raz w roku. | Al principio de cada año, por favor, envia una "FICHA DE INVENTARIO" actualizada a CIGRÉ | ažuriranu "Populacijsku karticu" svake godine istog datuma po vlastitom izboru. | ogni anno alla stessa data di vostra scelta una “SCHEDA POPOLAZIONE” aggiornata |  | CANADA | CA | CAN | 124
Ageing card for Capacitive Voltage Transformer |  |  | empty |  |  |  | an updated "POPULATION CARD" each year at an anniversary date of your choice. | aktualizovany prehled populace zarizeni kazdy rok k datu, který si vyberete | an updated "POPULATION CARD" each year at an anniversary date of your choice. | chaque année à une date anniversaire de votre choix une "carte de POPULATION" à jour, | Bitte senden Sie jedes Jahr ein aktualisiertes "Bestandsblatt" an die CIGRE. | ・毎年Ｃｉｇｒｅ本部にPopulation Card（台数調査票）のデータを更新してデータ提出を御願いします。 | Vær vennlig å send inn et oppdatert "Populasjons-skjema" til CIGRE hvert år | Uaktualnioną KARTĘ POPULACJI prosimy przesłać do CIGRE raz w roku. | Al principio de cada año, por favor, envia una "FICHA DE INVENTARIO" actualizada a CIGRÉ | ažuriranu "Populacijsku karticu" svake godine istog datuma po vlastitom izboru. | ogni anno alla stessa data di vostra scelta una “SCHEDA POPOLAZIONE” aggiornata |  | CANADA | CA | CAN | 124
Ageing Card for Magnetic Voltage Transformers and Current Transformers |  |  | empty |  |  | inputs available
Ageing Card for Combined Current and Voltage Transformers |  |  | empty |  |  | empty
Ageing card for Surge Arrester |  |  | empty
Ageing card for Shunt Capacitors |  |  | empty
Ageing card for Post Insulators |  |  | empty |  |  |  | The button with an embedded question mark is a link to a pertinent definition. | Pod tlacitkem s otaznikem se skryva definice | The button with an embedded question mark is a link to a pertinent definition. | Le bouton avec un point d'interrogation contient un lien d'aide pour une définition convenable | Der Button mit dem Fragezeichen ist ein Link zur passenden Definition | 定義が不明の項目については、”？”ボタンで詳細説明を御確認下さい。 | Knappen med et spørsmåltegn fører deg til en definisjon / forklaring. | Klawisz ze znakiem zapytania jest połączeniem do stosownej definicji | El botón con el signo de interrogación es un enlace a la correspondiente definición | Tipka s znakom upitnika predstavlja vezu sa pripadajućom definicijom. | Il pulsante con un punto di domanda è un collegamento ad una definizione | Butonul cu semnul "?" este o legatura catre o definitie pertinenta. | CHAD | TD | TCD | 148
[7 empty] | Error free? | Bez chyby? | Error free? | sans erreur ? | Fehlerfrei ? | Error free? | I orden? | Bez błędu? | ¿Sin errores? | Bez greške? | Senza errori? | Fara erori? | CHINA | CN | CHN | 156
[19 empty] | CHRISTMAS ISLAND | CX | CXR | 162
[19 empty] | COCOS (KEELING) ISLANDS | CC | CCK | 166
[7 empty] | Main Menu |  | Main Menu |  | Hauptmenü | [7 empty] | COLOMBIA | CO | COL | 170
[7 empty] | Which card do you want to fill out? | Jaky list dotazniku se chystate vyplnovat? | Which card do you want to fill out? | Quelle carte voulez-vous remplir ? | Welchen Kartentyp wollen Sie ausfüllen? | 入力するカードの「Go to」ボタンをクリック。 | Hvilken type skjema vil du fylle ut? | Którą kartę chcesz wypełnić? | ¿Qué ficha quiere rellenar? | Koju karticu želite popunjavati? | Che scheda volete compilare? | Ce fisa doriti sa completati? | COMOROS | KM | COM | 174
[6 empty] | Pointers | Population | Populace | Population | Population | Bestand | 台数調査 | Populasjon | Populacji | Inventario | Populacija | Popolazione | Populatie (volum) | CONGO | CG | COG | 178
[7 empty] | Failure | Porucha/zavada | Failure | Défaillance | Fehler | 故障調査 | Feil | Uszkodzenia | Fallo | Kvar | Guasto | Defectare | CONGO, THE DEMOCRATIC REPUBLIC OF THE | CD | COD | 180
[7 empty] | Circuit breakers | Vypinac SF6 | Circuit breakers | Disjoncteur | Leistungsschalter | Circuit Breaker （遮断器） | Effektbryter | Wyłącznika | Interruptor | SF6 prekidači | Interrutori in SF6 (Inclusi interruttori di circuito e di carico) | Intreruptoare in SF6 (inclusiv separatoare sub sarcina) | COOK ISLANDS | CK | COK | 184
[7 empty] | Load switches, | Zapouzdrena rozvodna | Load switches, | GIS | GIS | GIS | GIS | Rozdzielnicy GIS | Sub. Blindada | GIS (plinom izolirana postrojenja) | GIS | GIS | COSTA RICA | CR | CRI | 188
[7 empty] | Disconnects, | Odpojovac | Disconnects, | Sectionneur | Trennschalter | DS/ES （断路器／接地開閉器） | Skillebryter / jordslutter | Odłącznika | Seccionador | Rastavljači i zemljospojnici | Sezionatori e lame di terra | Separatoare si CLP | COTE D'IVOIRE | CI | CIV | 384
[7 empty] | earthing switches, | Uzemnovac | earthing switches, | MALT | Erdungsschalter | Earthing switch （接地開閉器） | Jordslutter | Uziemnika | Seccionador p.a.t. | Zemljospojnici | Sezionatori di terra | CLP | CROATIA (local name: Hrvatska) | HR | HRV | 191
[7 empty] | Conventional Instrument transformers (CT, VT, CT/VT, line traps), | Pristrojovy transformator | Conventional Instrument transformers (CT, VT, CT/VT, line traps), | Réducteur de mesure | Wandler | Instrument Transformer （計器用変成器） | Måletransformator | Przekładnika | Transformador de medida | Mjerni transformatori | Trasformatori di misura | Transformatoare de masura | CUBA | CU | CUB | 192
[7 empty] | Surge Arresters, | Hlavni nabidka | Surge Arresters, | Menu Principal | Hauptmenü | メインメニュー | Hovedmeny | Główne menu | Menu principal | Glavni izbornik | Menù Principale | Meniul principal | CYPRUS | CY | CYP | 196
[7 empty] | Post insulators | Pomoc | Post insulators | Aide | Hilfe | Help | Hjelp | Pomoc | Ayuda | Pomoć | Guida | Help | CZECH REPUBLIC | CZ | CZE | 203
[7 empty] | Shunt/series reactors, | Udrzba | Shunt/series reactors, | Maintenance | Wartung | 保守・点検 | Maintenance | Obsługi | Mantenimiento | Održavanje | Manutenzione | Mentenanta | DENMARK | DK | DNK | 208
[7 empty] | Capacitor banks, |  | Capacitor banks, | [9 empty] | DJIBOUTI | DJ | DJI | 262
[6 empty] | Part of file name | Other substation equipment e.g. busbar conductors and accessories etc. |  | Other substation equipment e.g. busbar conductors and accessories etc. | [9 empty] | DOMINICA | DM | DMA | 212
[6 empty] | 2013_0_0_GH9 | [12 empty] | DOMINICAN REPUBLIC | DO | DOM | 214
[6 empty] | 2013 | [12 empty] | EAST TIMOR | TP | TMP | 626
[6 empty] | 0 | [12 empty] | ECUADOR | EC | ECU | 218
[6 empty] | 0 | [12 empty] | EGYPT | EG | EGY | 818
[6 empty] | G | [12 empty] | EL SALVADOR | SV | SLV | 222
[6 empty] | H | Send to CIGRE ? | Odeslat CIGRE? | Send to CIGRE ? | Envoyer à CIGRE? | An CIGRE senden ? | CIGREに送付 ? | Send til CIGRE? | Wysłać do CIGRE | Send to CIGRE ? | Poslati CIGRE-u? | Send to CIGRE ? | Trimiteti la CIGRE? | EQUATORIAL GUINEA | GQ | GNQ | 226
[6 empty] | 9 | No | Ne | No | Non | Nein | いいえ | Nei | Nie | No | Ne | No | Nu | ERITREA | ER | ERI | 232
[6 empty] | 16 | Do you want to save only this card and send it back to CIGRE ? | Chcete ulozit pouze tuto kartu (list) pred tim, nez ji zaslete zpet Cigre? | Do you want to save only this card and send it back to CIGRE ? | Voulez vous sauvegarder uniquement cette carte et la renvoyer à la CIGRE ? | Wollen Sie nur diese Karte speichern und sie an die CIGRE zurückschicken ? | Cigre本部に返送する前に、この調査票のみを保存しますか？ | Ønsker du å lagre kun dette skjemaet før du returnerer det til CIGRE? | Czy tylko tą Kartę zapisać przed wysłaniem do CIGRE? | ¿Quiere salvar solo esta ficha antes de enviarla a CIGRÉ? | Želite li spremiti samo ovu karticu prije slanja natrag u CIGRE ? | Do you want to save only this card and send it back to CIGRE ? | Doriti sa salvati numai aceasta fisa si s-o trimiteti inapoi la CIGRE? | ESTONIA | EE | EST | 233
[6 empty] | 17 | [12 empty] | ETHIOPIA | ET | ETH | 231
[6 empty] | 9 | [12 empty] | FALKLAND ISLANDS (MALVINAS) | FK | FLK | 238
[6 empty] | 21357 | [12 empty] | FAROE ISLANDS | FO | FRO | 234
[6 empty] | day | [12 empty] | FIJI | FJ | FJI | 242
[6 empty] | 41779 | [12 empty] | FINLAND | FI | FIN | 246
[6 empty] | parity(min) | [12 empty] | FRANCE | FR | FRA | 250
[6 empty] | 1 | [12 empty] | France METROPOLITAN | FX | FXX | 249
[6 empty] | sec | [12 empty] | FRENCH GUIANA | GF | GUF | 254
[6 empty] | 9 | [12 empty] | FRENCH POLYNESIA | PF | PYF | 258
[19 empty] | FRENCH SOUTHERN TERRITORIES | TF | ATF | 260
[19 empty] | GABON | GA | GAB | 266
[19 empty] | GAMBIA | GM | GMB | 270
[19 empty] | GEORGIA | GE | GEO | 268
[19 empty] | GERMANY | DE | DEU | 276
[19 empty] | GHANA | GH | GHA | 288
[19 empty] | GIBRALTAR | GI | GIB | 292
[19 empty] | GREECE | GR | GRC | 300
[19 empty] | GREENLAND | GL | GRL | 304
[19 empty] | GRENADA | GD | GRD | 308
[19 empty] | GUADELOUPE | GP | GLP | 312
[19 empty] | GUAM | GU | GUM | 316
[19 empty] | GUATEMALA | GT | GTM | 320
[19 empty] | GUINEA | GN | GIN | 324
[19 empty] | GUINEA-BISSAU | GW | GNB | 624
[19 empty] | GUYANA | GY | GUY | 328
[19 empty] | HAITI | HT | HTI | 332
[19 empty] | HEARD AND MC DONALD ISLANDS | HM | HMD | 334
[19 empty] | HONDURAS | HN | HND | 340
[19 empty] | HONG KONG | HK | HKG | 344
[19 empty] | HUNGARY | HU | HUN | 348
[19 empty] | ICELAND | IS | ISL | 352
[19 empty] | INDIA | IN | IND | 356
[19 empty] | INDONESIA | ID | IDN | 360
[19 empty] | IRAN (ISLAMIC REPUBLIC OF) | IR | IRN | 364
[19 empty] | IRAQ | IQ | IRQ | 368
[19 empty] | IRELAND | IE | IRL | 372
[19 empty] | ISRAEL | IL | ISR | 376
[19 empty] | ITALY | IT | ITA | 380
[19 empty] | JAMAICA | JM | JAM | 388
[19 empty] | JAPAN | JP | JPN | 392
[19 empty] | JORDAN | JO | JOR | 400
[19 empty] | KAZAKHSTAN | KZ | KAZ | 398
[19 empty] | KENYA | KE | KEN | 404
[19 empty] | KIRIBATI | KI | KIR | 296
[19 empty] | KOREA, DEMOCRATIC PEOPLE'S REPUBLIC OF | KP | PRK | 408
[19 empty] | KOREA, REPUBLIC OF | KR | KOR | 410
[19 empty] | KUWAIT | KW | KWT | 414
[19 empty] | KYRGYZSTAN | KG | KGZ | 417
[19 empty] | LAO PEOPLE'S DEMOCRATIC REPUBLIC | LA | LAO | 418
[19 empty] | LATVIA | LV | LVA | 428
[19 empty] | LEBANON | LB | LBN | 422
[19 empty] | LESOTHO | LS | LSO | 426
[19 empty] | LIBERIA | LR | LBR | 430
[19 empty] | LIBYAN ARAB JAMAHIRIYA | LY | LBY | 434
[19 empty] | LIECHTENSTEIN | LI | LIE | 438
[19 empty] | LITHUANIA | LT | LTU | 440
[19 empty] | LUXEMBOURG | LU | LUX | 442
[19 empty] | MACAU | MO | MAC | 446
[19 empty] | MACEDONIA, THE FORMER YUGOSLAV REPUBLIC OF | MK | MKD | 807
[19 empty] | MADAGASCAR | MG | MDG | 450
[19 empty] | MALAWI | MW | MWI | 454
[19 empty] | MALAYSIA | MY | MYS | 458
[19 empty] | MALDIVES | MV | MDV | 462
[19 empty] | MALI | ML | MLI | 466
[19 empty] | MALTA | MT | MLT | 470
[19 empty] | MARSHALL ISLANDS | MH | MHL | 584
[19 empty] | MARTINIQUE | MQ | MTQ | 474
[19 empty] | MAURITANIA | MR | MRT | 478
[19 empty] | MAURITIUS | MU | MUS | 480
[19 empty] | MAYOTTE | YT | MYT | 175
[19 empty] | MEXICO | MX | MEX | 484
[19 empty] | MICRONESIA, FEDERATED STATES OF | FM | FSM | 583
[19 empty] | MOLDOVA, REPUBLIC OF | MD | MDA | 498
[19 empty] | MONACO | MC | MCO | 492
[19 empty] | MONGOLIA | MN | MNG | 496
[19 empty] | MONTSERRAT | MS | MSR | 500
[19 empty] | MOROCCO | MA | MAR | 504
[19 empty] | MOZAMBIQUE | MZ | MOZ | 508
[19 empty] | MYANMAR | MM | MMR | 104
[19 empty] | NAMIBIA | NA | NAM | 516
[19 empty] | NAURU | NR | NRU | 520
[19 empty] | NEPAL | NP | NPL | 524
[19 empty] | NETHERLANDS | NL | NLD | 528
[19 empty] | NETHERLANDS ANTILLES | AN | ANT | 530
[19 empty] | NEW CALEDONIA | NC | NCL | 540
[19 empty] | NEW ZEALAND | NZ | NZL | 554
[19 empty] | NICARAGUA | NI | NIC | 558
[19 empty] | NIGER | NE | NER | 562
[19 empty] | NIGERIA | NG | NGA | 566
[19 empty] | NIUE | NU | NIU | 570
[19 empty] | NORFOLK ISLAND | NF | NFK | 574
[19 empty] | NORTHERN MARIANA ISLANDS | MP | MNP | 580
[19 empty] | NORWAY | NO | NOR | 578
[19 empty] | OMAN | OM | OMN | 512
[19 empty] | PAKISTAN | PK | PAK | 586
[19 empty] | PALAU | PW | PLW | 585
[19 empty] | PANAMA | PA | PAN | 591
[19 empty] | PAPUA NEW GUINEA | PG | PNG | 598
[19 empty] | PARAGUAY | PY | PRY | 600
[19 empty] | PERU | PE | PER | 604
[19 empty] | PHILIPPINES | PH | PHL | 608
[19 empty] | PITCAIRN | PN | PCN | 612
[19 empty] | POLAND | PL | POL | 616
[19 empty] | PORTUGAL | PT | PRT | 620
[19 empty] | PUERTO RICO | PR | PRI | 630
[19 empty] | QATAR | QA | QAT | 634
[19 empty] | REUNION | RE | REU | 638
[19 empty] | ROMANIA | RO | ROM | 642
[19 empty] | RUSSIAN FEDERATION | RU | RUS | 643
[19 empty] | RWANDA | RW | RWA | 646
[19 empty] | SAINT KITTS AND NEVIS | KN | KNA | 659
[19 empty] | SAINT LUCIA | LC | LCA | 662
[19 empty] | SAINT VINCENT AND THE GRENADINES | VC | VCT | 670
[19 empty] | SAMOA | WS | WSM | 882
[19 empty] | SAN MARINO | SM | SMR | 674
[19 empty] | SAO TOME AND PRINCIPE | ST | STP | 678
[19 empty] | SAUDI ARABIA | SA | SAU | 682
[19 empty] | SENEGAL | SN | SEN | 686
[19 empty] | SEYCHELLES | SC | SYC | 690
[19 empty] | SIERRA LEONE | SL | SLE | 694
[19 empty] | SINGAPORE | SG | SGP | 702
[19 empty] | SLOVAKIA (Slovak Republic) | SK | SVK | 703
[19 empty] | SLOVENIA | SI | SVN | 705
[19 empty] | SOLOMON ISLANDS | SB | SLB | 90
[19 empty] | SOMALIA | SO | SOM | 706
[19 empty] | SOUTH AFRICA | ZA | ZAF | 710
[19 empty] | SOUTH GEORGIA AND THE SOUTH SANDWICH ISLANDS | GS | SGS | 239
[19 empty] | SPAIN | ES | ESP | 724
[19 empty] | SRI LANKA | LK | LKA | 144
[19 empty] | ST. HELENA | SH | SHN | 654
[19 empty] | ST. PIERRE AND MIQUELON | PM | SPM | 666
[19 empty] | SUDAN | SD | SDN | 736
[19 empty] | SURINAME | SR | SUR | 740
[19 empty] | SVALBARD AND JAN MAYEN ISLANDS | SJ | SJM | 744
[19 empty] | SWAZILAND | SZ | SWZ | 748
[19 empty] | SWEDEN | SE | SWE | 752
[19 empty] | SWITZERLAND | CH | CHE | 756
[19 empty] | SYRIAN ARAB REPUBLIC | SY | SYR | 760
[19 empty] | TAIWAN, PROVINCE OF CHINA | TW | TWN | 158
[19 empty] | TAJIKISTAN | TJ | TJK | 762
[19 empty] | TANZANIA, UNITED REPUBLIC OF | TZ | TZA | 834
[19 empty] | THAILAND | TH | THA | 764
[19 empty] | TOGO | TG | TGO | 768
[19 empty] | TOKELAU | TK | TKL | 772
[19 empty] | TONGA | TO | TON | 776
[19 empty] | TRINIDAD AND TOBAGO | TT | TTO | 780
[19 empty] | TUNISIA | TN | TUN | 788
[19 empty] | TURKEY | TR | TUR | 792
[19 empty] | TURKMENISTAN | TM | TKM | 795
[19 empty] | TURKS AND CAICOS ISLANDS | TC | TCA | 796
[19 empty] | TUVALU | TV | TUV | 798
[19 empty] | UGANDA | UG | UGA | 800
[19 empty] | UKRAINE | UA | UKR | 804
[19 empty] | UNITED ARAB EMIRATES | AE | ARE | 784
[19 empty] | UNITED KINGDOM | GB | GBR | 826
[19 empty] | UNITED STATES | US | USA | 840
[19 empty] | UNITED STATES MINOR OUTLYING ISLANDS | UM | UMI | 581
[19 empty] | URUGUAY | UY | URY | 858
[19 empty] | UZBEKISTAN | UZ | UZB | 860
[19 empty] | VANUATU | VU | VUT | 548
[19 empty] | VATICAN CITY STATE (HOLY SEE) | VA | VAT | 336
[19 empty] | VENEZUELA | VE | VEN | 862
[19 empty] | VIET NAM | VN | VNM | 704
[19 empty] | VIRGIN ISLANDS (BRITISH) | VG | VGB | 92
[19 empty] | VIRGIN ISLANDS (U.S.) | VI | VIR | 850
[19 empty] | WALLIS AND FUTUNA ISLANDS | WF | WLF | 876
[19 empty] | WESTERN SAHARA | EH | ESH | 732
[19 empty] | YEMEN | YE | YEM | 887
[19 empty] | YUGOSLAVIA | YU | YUG | 891
[19 empty] | ZAMBIA | ZM | ZMB | 894
[19 empty] | ZIMBABWE | ZW | ZWE | 716
[21 empty] | language | column number on sheets
[21 empty] | Cestina | 1
[21 empty] | Deutsch | 4
[21 empty] | English | 2
[21 empty] | Espagñol | 8
[21 empty] | Français | 3
[21 empty] | Hrvatski (Croatian) | 9
[21 empty] | Italiano | 10
[21 empty] | Japanese | 5
[21 empty] | Norsk | 6
[21 empty] | Polski | 7
[21 empty] | Română | 11
[21 empty] | ? | 12
Note on L1: WG: Orange fields contain formulae ! Delete answer in the questionnaire !
Note on M74: WG: system generated number 366*2*60=43920~36^3 -> one can make max 120 save operations without having the same file name.
Note on M70: WG: in base 36
Note on AE243: WG: to modify order in drop-down menu, change a complete line in the table.

## GI
General Information about Asset Management of High Voltage Equipment |  |  |  | Has the form been filled out?
EQUIPMENT INFORMATION EXCHANGE WITH MANUFACTURERS |  |  |  | 0
| Do you RECEIVE an expected technical life time from manufacturer? | Do you RECEIVE instruction manuals for performing maintenance, diagnostics and monitoring?
0
If YES: Do the manufacturers update this information over the life time |  |  | yes | 0
If YES: Do you use this for asset management decisions |  |  | no
If YES: Do you strictly fulfil the manufacturers recommendations
If NOT, would you like to receive it
informally - national
via formal national forum
If you RECEIVE the instructions, do these instructions include? | Multiple choice |  | informally - international
Conditions of when the diagnostic measurement is to be performed |  |  | via international organization (please specify below)
Description of the diagnostic measurement method and measurement conditions
Description of how to evaluate diagnostic measurements and what further activity has to be adopted
Description of how to evaluate monitored parameters and what further activity has to be adopted
Description of residual life calculation
Do you provide feedback on equipment performance experience to the manufacturers? |  |  |  | 0
if not are you willing to provide
EQUIPMENT INFORMATION EXCHANGE WITH UTILITIES |  |  | separated files
central DB
Exchange of information with other users exists: (formal, informal, international societies, ...) |  |  | other (please specify below) | 0
If YES in what form
none
DATA COLLECTED OVER ASSET LIFE CYCLE |  |  | ad hoc analysis
periodical analysis
Do you collect data over the life time of the equipment? |  |  | automatic permanent evaluation | 0
other (please specify below)
What data is collected and evaluated | Multiple choice
actual conditions (by diagnostic measurement or monitoring)
life time stress
age |  |  | Technical aspects
history of the equipment behaviour (number of major and minor failures) |  |  | Strategic aspects
history of the same technological type group |  |  | Financial aspects
maintainability and repairability |  |  | Legal aspects
other (please, specify)
How is it collected | Multiple choice
periodical diagnostic measurement
occasional diagnostic measurement
on/line monitoring
forensic analysis
other (please, specify)
How is the data stored
CONDITION ASSESSMENT TECHNIQUES, APPLICATION AND USE
How the condition data about equipment is evaluated? |  |  |  | 0
What is the output of the evaluation? | Multiple choice
report |  |  |  | 0
health index |  |  |  | 0
ageing curve |  |  |  | 0
remaining life time calculation |  |  |  | 0
other (please, specify)
Please answer the following questions as free text
What do expect (how do you interpret the health index)? |  |  |  | 0
What aspects does the health index include? |  |  |  | 0
How is the health index calculated? |  |  |  | 0
What values can the health index attain and what are their meanings? |  |  |  | 0
How are the health index values used (what is this information used for) ? |  |  |  | 0
ASSET MANAGEMENT DECISION MAKING MODELS AND MITIGATION TECHNIQUES
Main driving strategy for planned ageing mitigation techniques |  |  |  | 0
Strategies applied to manage ageing equipment | Multiple choice
Age based only |  |  |  | 0
Actual service conditions based |  |  |  | 0
Experience based |  |  |  | 0
Life time management (economical calculations) |  |  |  | 0
Residual life based |  |  |  | 0
Risk and criticality based (importance of the installation place) |  |  |  | 0
Substation refurbishment and investment plans |  |  |  | 0
Repairability (spares and spare units considerations incl.) |  |  |  | 0
Other, please, specify |  |  |  | 0
The decision making process usually concerns
recommendation for consideration for individual equipment |  |  |  | 0
for group of equipment |  |  |  | 0
Decision making tools/models
Intuitive (supported by reports and written analyses) |  |  |  | 0
Information technology (SW - please describe) |  |  |  | 0
Other (please, describe) |  |  |  | 0
NEW APPROACHES AND FUTURE PLANS
Plans for the future
to keep present state |  |  |  | 0
to develop something new |  |  |  | 0
if yes, what?

## CB_G_A
|  | Ageing Card for Gas Circuit Breakers (excluding: GIS equipment) |  |  | A0 - Electrical Degradation A1 - - Shift of resistance/ overheating A2 - - Loss of dielectric strength A3 - - Reduced short circuit breaking capability A4 - - Change of Capacitance B0 - Mechanical degradation B1 - - Wear B2 - - Fatigue B3 - - Relaxation B4 - - Mechanical loosening B5 - - Loose / sticking contacts B6 - - Oil leakage B7 - - Media leakage (SF6, oil, air) C0 - Material degradation C1 - - Corrosion C2 - - Contamination C3 - - Chemical reaction with media decomposition by-products C4 - - Grease degradation / loss of lubrication C5 - - Increase of moisture D0 - Others D1 - - Disturbed / drifting settings D0 - - Other phenomena, please specify | F0 - Electrical stress F1 - - Electric voltage stress F2 - - Breaking current G0 - Dielectric stress G1 - - Degradation and contamination of oil media H0 - Mechanical stress H1 - - Mechanical loads H2 - - Number of operations I0 - Environmental influence I1 - - Temperature I2 - - Water ingress J0 - Others J1 - - Presence of media decomposition by-products J1 - - Improper or lack of maintenance J2 - - Other factors, please specify | Ma1 - Does not operate on command Ma2 - Operates without command Ma3 - Electrical breakdown Ma4 - Locking in open or close position Ma5 - Other major failure consequence, please specify Mi1 - Air or hydraulic oil leakage in the operating mechanism Mi2 - Small SF6 leakage Mi3 - Oil leakage of grading capacitors Mi4 - Change in mechanical functional characteristics Mi5 - Change in electrical functional characteristics Mi6 - Change in functional characteristics of control or auxiliary systems Mi7 - Other minor failure consequence, please specify | D01 - Visual inspection （intrusive/overhaul) D02 - Voltage drop measurement (static resistance) D03 - Dynamic resistance measurement; D04 - Monitoring of interruption current D05 - No-load operation with measurement of characteristics D06 - SF6-gas analysis (moisture / decomposition products / gas percentage) D07 - Tightness measurement (gas or oil) D08 - Terminal load measurement (bending) D09 - High voltage test on site D10 - Partial Discharge measurement D11 - Insulation resistance measurement D12 - Measurement of the quantity of repumping cycles D13 - Measurement of oil pressure drop D14 - Oil quality measurement D15 - Supervision of control circuits D16 - Monitoring of current waveform D17 - IR-Thermography D18 - Other detection techniques, please specify | M01 - Overhaul / servicing M02 - Replacement with new or improved parts M03 - Installation of monitoring M04 - Other mitigation techniques, please specify | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | Optional subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing, what failure modes has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the circuit breaker life was the reported ageing phenomenon experienced | no | 0
| e.g. | Component at service voltage | Making and breaking units | Main contact | A1 | H2 | Ma5 (fails to carry current) | D02 | M02 |  | 10…30
x | no | Component at service voltage | [10 empty] | 0
x | no | Component at service voltage | Making and breaking units | [9 empty] | 0
x | no | Component at service voltage | Making and breaking units | Main contact | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Nozzle/arcing contacts | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Puffer cylinder | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Grease, lubrication | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Other parts of the making and breaking units | [8 empty] | 0
x | no | Component at service voltage | Auxiliary interrupters (making or breaking) and resistors | [9 empty] | 0
x | no | Component at service voltage | Auxiliary interrupters (making or breaking) and resistors | Main contact | [8 empty] | 0
x | no | Component at service voltage | Auxiliary interrupters (making or breaking) and resistors | Resistors | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | [9 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Interrupter chamber, including insulators | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Bushing, porcelain and composite | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Metal Enclosure | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | SF6 gas | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Sealing-O-ring, flange, operation rod seal, etc. | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Insulating operation rod, inter-connecting/coupling pin and linkage | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Surge arrestor (if applicable) | [8 empty] | 0
x | no | Component at service voltage | Grading capacitors | [9 empty] | 0
x | no | Component at service voltage | Grading capacitors | Capacitor element | [8 empty] | 0
x | no | Component at service voltage | Grading capacitors | capacitor sealing's | [8 empty] | 0
x | no | Component at service voltage | Other parts of components at service voltage | [9 empty] | 0
x | no | Component at service voltage | Other parts of components at service voltage | Adsorbent, other, please specify | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | [10 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Tripping and closing circuits | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Tripping and closing circuits | Coil/plunger - please specify | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Tripping and closing circuits | Capacitors | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Auxiliary switches and associated drives | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Electrical components | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Electrical components | Relays, contactors, thermostats, fuses, wiring, other - please specify | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Heaters | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Gas density supervision | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Gas density supervision | Gas density monitor | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Gas density supervision | Pressure gauge | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Gas density supervision | Gas-piping and non-return valves | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Other monitoring systems (including sensors) | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Bushing current transformer | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Other part of electrical control and auxiliary circuits | [9 empty] | 0
x | no | Operating mechanism (earthed) | [10 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | Compressors, motors, pumps | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | Piping | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | Seal packing | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | O-ring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | other | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Spring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Piston | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Cylinder | [8 empty] | 0
| no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | O-ring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Other - please specify | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | [9 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Piston, cylinder | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Seal packing, O-ring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Fluid medium | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Spring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Grease, Lubrication | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Other - please specify | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Mechanical part | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Housing | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Shaft | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Shaft-Seal packing | [8 empty] | 0
| no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Grease, Lubrication | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Other - please specify | [8 empty] | 0
x | no | Kinematic chain | [10 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | [9 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Mechanical linkages, bearings, and pin parts | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Shaft | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Housing, base frame, and covers | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Seal | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Lubrication, grease | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Other - please specify

## CB_O_A
|  | Ageing Card for Oil Circuit Breakers (excluding: GIS equipment) |  |  | A0 - Electrical Degradation A1 - - Shift of resistance/ overheating A2 - - Loss of dielectric strength A3 - - Reduced short circuit breaking capability A4 - - Change of Capacitance B0 - Mechanical degradation B1 - - Wear B2 - - Fatigue B3 - - Relaxation B4 - - Mechanical loosening B5 - - Loose / sticking contacts B6 - - Oil leakage B7 - - Media leakage (SF6, oil, air) C0 - Material degradation C1 - - Corrosion C2 - - Contamination C3 - - Chemical reaction with media decomposition by-products C4 - - Grease degradation / loss of lubrication C5 - - Increase of moisture D0 - Others D1 - - Disturbed / drifting settings D0 - - Other phenomena, please specify | F0 - Electrical stress F1 - - Electric voltage stress F2 - - Breaking current G0 - Dielectric stress G1 - - Degradation and contamination of oil media H0 - Mechanical stress H1 - - Mechanical loads H2 - - Number of operations I0 - Environmental influence I1 - - Temperature I2 - - Water ingress J0 - Others J1 - - Presence of media decomposition by-products J1 - - Improper or lack of maintenance J2 - - Other factors, please specify | Ma1 - Does not operate on command Ma2 - Operates without command Ma3 - Electrical breakdown Ma4 - Locking in open or close position Ma5 - Other major failure consequence, please specify Mi1 - Air or hydraulic oil leakage in the operating mechanism Mi2 - Small SF6 leakage Mi3 - Oil leakage of grading capacitors Mi4 - Change in mechanical functional characteristics Mi5 - Change in electrical functional characteristics Mi6 - Change in functional characteristics of control or auxiliary systems Mi7 - Other minor failure consequence, please specify | D01 - Visual inspection （intrusive/overhaul) D02 - Voltage drop measurement (static resistance) D03 - Dynamic resistance measurement; D04 - Monitoring of interruption current D05 - No-load operation with measurement of characteristics D06 - SF6-gas analysis (moisture / decomposition products / gas percentage) D07 - Tightness measurement (gas or oil) D08 - Terminal load measurement (bending) D09 - High voltage test on site D10 - Partial Discharge measurement D11 - Insulation resistance measurement D12 - Measurement of the quantity of repumping cycles D13 - Measurement of oil pressure drop D14 - Oil quality measurement D15 - Supervision of control circuits D16 - Monitoring of current waveform D17 - IR-Thermography D18 - Other detection techniques, please specify | M01 - Overhaul / servicing M02 - Replacement with new or improved parts M03 - Installation of monitoring M04 - Other mitigation techniques, please specify | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | Optional subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing, what failure modes has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the equipment life was the reported ageing phenomenon experienced? | no | 0
| e.g.. | Component at service voltage | Making and breaking units | Main contact | A1 | H2 | Ma5 (fails to carry current) | D02 | M02 |  | 10…30
x | no | Component at service voltage | [10 empty] | 0
x | no | Component at service voltage | Making and breaking units | [9 empty] | 0
x | no | Component at service voltage | Making and breaking units | Main contact | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Arcing contacts | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Arc chamber, arc control device | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Other parts of the making and breaking units | [8 empty] | 0
x | no | Component at service voltage | Auxiliary interrupters (making or breaking) and resistors | [9 empty] | 0
x | no | Component at service voltage | Auxiliary interrupters (making or breaking) and resistors | Main contact | [8 empty] | 0
x | no | Component at service voltage | Auxiliary interrupters (making or breaking) and resistors | Resistors | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | [9 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Interrupter assembly, including insulation | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | External Bushing, (porcelain) | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Metal Enclosure (Bulk oil) | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Oil media | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Support & rotating insulators (Min oil) | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Insulating operation rod | [8 empty] | 0
x | no | Component at service voltage | Grading capacitors | [9 empty] | 0
x | no | Component at service voltage | Grading capacitors | Capacitor element | [8 empty] | 0
x | no | Component at service voltage | Grading capacitors | capacitor sealing's | [8 empty] | 0
x | no | Component at service voltage | Other parts of components at service voltage | [9 empty] | 0
x | no | Component at service voltage | Other parts of components at service voltage | Please specify | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Tripping and closing circuits | Coil/plunger - please specify | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Tripping and closing circuits | Capacitors | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Auxiliary switches and associated drives | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Electrical components | Relays, contactors, thermostats, fuses, wiring, other - please specify | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Heaters | Heaters & thermostats | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Other monitoring systems (including sensors) | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Bushing current transformer | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Other part of electrical control and auxiliary circuits | Please specify | [8 empty] | 0
x | no | Operating mechanism (earthed) | [10 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | Compressors, motors | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | Piping | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | Seal packing, O-ring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | other | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Spring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Piston, cylinder | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | O-ring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Other - please specify | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | [9 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Piston, cylinder | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Seal packing, O-ring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Fluid medium | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Spring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Lubrication, Grease | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Other - please specify | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Mechanical part | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Shaft-Seal packing | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Shaft | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Housing | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Lubrication, Grease | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Other - please specify | [8 empty] | 0
x | no | Kinematic chain | [10 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | [9 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Mechanical part | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Shaft | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Seal | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Housing | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Lubrication, grease | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Other - please specify | [8 empty] | 0

## CB_A_A
|  | Ageing Card for Air blast Circuit Breakers |  |  | A0 - Electrical Degradation A1 - - Shift of resistance/ overheating A2 - - Loss of dielectric strength A3 - - Reduced short circuit breaking capability A4 - - Change of Capacitance B0 - Mechanical degradation B1 - - Wear B2 - - Fatigue B3 - - Relaxation B4 - - Mechanical loosening B5 - - Loose / sticking contacts B6 - - Oil leakage B7 - - Media leakage (SF6, oil, air) C0 - Material degradation C1 - - Corrosion C2 - - Contamination C3 - - Chemical reaction with media decomposition by-products C4 - - Grease degradation / loss of lubrication C5 - - Increase of moisture D0 - Others D1 - - Disturbed / drifting settings D0 - - Other phenomena, please specify | F0 - Electrical stress F1 - - Electric voltage stress F2 - - Breaking current G0 - Dielectric stress G1 - - Degradation and contamination of oil media H0 - Mechanical stress H1 - - Mechanical loads H2 - - Number of operations I0 - Environmental influence I1 - - Temperature I2 - - Water ingress J0 - Others J1 - - Presence of media decomposition by-products J1 - - Improper or lack of maintenance J2 - - Other factors, please specify | Ma1 - Does not operate on command Ma2 - Operates without command Ma3 - Electrical breakdown Ma4 - Locking in open or close position Ma5 - Other major failure consequence, please specify Mi1 - Air or hydraulic oil leakage in the operating mechanism Mi2 - Small SF6 leakage Mi3 - Oil leakage of grading capacitors Mi4 - Change in mechanical functional characteristics Mi5 - Change in electrical functional characteristics Mi6 - Change in functional characteristics of control or auxiliary systems Mi7 - Other minor failure consequence, please specify | D01 - Visual inspection （intrusive/overhaul) D02 - Voltage drop measurement (static resistance) D03 - Dynamic resistance measurement; D04 - Monitoring of interruption current D05 - No-load operation with measurement of characteristics D06 - SF6-gas analysis (moisture / decomposition products / gas percentage) D07 - Tightness measurement (gas or oil) D08 - Terminal load measurement (bending) D09 - High voltage test on site D10 - Partial Discharge measurement D11 - Insulation resistance measurement D12 - Measurement of the quantity of repumping cycles D13 - Measurement of oil pressure drop D14 - Oil quality measurement D15 - Supervision of control circuits D16 - Monitoring of current waveform D17 - IR-Thermography D18 - Other detection techniques, please specify | M01 - Overhaul / servicing M02 - Replacement with new or improved parts M03 - Installation of monitoring M04 - Other mitigation techniques, please specify | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | Optional subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing, what failure modes has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the circuit breaker life was the reported ageing phenomenon experienced | no | 0
x | e... | Component at service voltage | Making and breaking units | Main contact | A1 | H2 | Ma5 (fails to carry current) | D02 | M02 |  | 10…30
x | no | Component at service voltage | [10 empty] | 0
x | no | Component at service voltage | Making and breaking units | [9 empty] | 0
x | no | Component at service voltage | Making and breaking units | Main contact | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Nozzle/arcing contacts | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Grease, lubrication | [8 empty] | 0
x | no | Component at service voltage | Making and breaking units | Other parts of the making and breaking units | [8 empty] | 0
x | no | Component at service voltage | Auxiliary interrupters (making or breaking) and resistors | [9 empty] | 0
x | no | Component at service voltage | Auxiliary interrupters (making or breaking) and resistors | Main contact | [8 empty] | 0
x | no | Component at service voltage | Auxiliary interrupters (making or breaking) and resistors | Resistors | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | [9 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Interrupter chamber, including insulators | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Bushing, porcelain and/or composite | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Metal Enclosure | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Air (insulating media) | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Sealing-O-ring, flange, operation rod seal, etc. | [8 empty] | 0
x | no | Component at service voltage | Main insulation to earth (including bushings, pull rods and pipes, etc.) | Insulating operation rod | [8 empty] | 0
x | no | Component at service voltage | Grading capacitors | [9 empty] | 0
x | no | Component at service voltage | Grading capacitors | Capacitor element | [8 empty] | 0
x | no | Component at service voltage | Grading capacitors | capacitor sealing's | [8 empty] | 0
x | no | Component at service voltage | Other parts of components at service voltage | Adsorbent, other, please specify | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | [10 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Tripping and closing circuits | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Tripping and closing circuits | Coil/plunger - please specify | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Tripping and closing circuits | Capacitors | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Auxiliary switches and associated drives | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Electrical components | Relays, contactors, thermostats, fuses, wiring, other - please specify | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Heaters | Heaters & thermostats | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Other monitoring systems (including sensors) | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Bushing current transformer | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of circuit breaker) | Other part of electrical control and auxiliary circuits | Please specify | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | Compressors, motors | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | Piping | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | Seal packing, O-ring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Compressors, motors, pumps, piping fittings (when part of circuit breaker) | other | [8 empty] | 0
x | no | Operating mechanism (earthed) | [10 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Spring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Piston, cylinder | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | O-ring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | Other - please specify | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | [9 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Piston, cylinder | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Seal packing, O-ring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Spring | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Lubrication, Grease | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | Other - please specify | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Mechanical part | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Shaft-Seal packing | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Shaft | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Housing | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Lubrication, Grease | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism) | Other - please specify | [8 empty] | 0
x | no | Kinematic chain | [10 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | [9 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Mechanical part | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Shaft | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Seal | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Housing | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Lubrication, grease | [8 empty] | 0
x | no | Kinematic chain | Kinematic chain (mechanical transmission elements between operating mechanism and main units) | Other - please specify | [8 empty] | 0
x | no | High pressure air system | [10 empty] | 0
x | no | High pressure air system | High pressure air system | [9 empty] | 0
x | no | High pressure air system | High pressure air system | Air cylinder | [8 empty] | 0
x | no | High pressure air system | High pressure air system | Blast valve | [8 empty] | 0
x | no | High pressure air system | High pressure air system | Air piping | [8 empty] | 0
x | no | High pressure air system | High pressure air system | Sealing-O-ring, flange, etc. | [8 empty] | 0
x | no | High pressure air system | High pressure air system | Pressure gauge | [8 empty] | 0

## DS_A
|  | Ageing Card for Disconnectors and Earthing Switches (excluding: Disconnecting Circuit Breakers, oil or pressure air insulated equipment, GIS equipment) |  | A0 - Electrical degradation A1 - - Change of resistance A2 - - Electrical treeing A3 - - Welding B0 - Mechanical degradation B1 - - Deformation B2 - - Cracking B3 - - Breaking B4 - - Abrasion B5 - - Loosening of loading force C0 - Material degradation C1 - - Corrosion C2 - - Oxidation C3 - - Loss of lubrication C4 - - Erosion D0 - Others | F0 - Electrical stresses F1 - - Switching voltages/currents F2 - - Lightning voltages/currents H0 - Mechanical stresses H1 - - Number of operations H2 - - Vibrations I1 - Environmental influence I2 - - Rain I3 - - Moisture I4 - - Dust I5 - - UV radiation I6 - - Temperature I7 - - Wind J0 - Others | Mi0 - Minor Failure Modes Mi1 - - overheat Mi2 - - misalignment Mi3 - - loss of initial settings Mi4 - - Other Ma0 - Major Failure Modes Ma1 - - Does not close/open on command Ma2 - - Closes/Opens without command Ma3 - - Fails to carry current Ma4 - - Breakdown to earth Ma5 - - Locked in open/closed position Ma6 - - Loss of mechanical integrity Ma7 - - Other | R0 - Visual inspection R1 - Thermographic inspection R2 - Resistance measurement R3 - Current-time profile R4 - Torque-time profile R5 - Time measurement R6 - Force or pressure measurement R7 - Other mechanical and electrical tests | Q0 - Complete unit replacement Q1 - Component replacement Q2 - Surface Treatment Q3 - Readjustment Q4 - Cleaning Q5 - Regreasing Q6 - Other | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing, what failure modes has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the equipment life was the reported ageing phenomenon experienced? | no | 0
| e.g. | Operating mechanism (earthed) | Electrical motors | C1, D0-burned | H1, I2, I5 | Ma1, Ma5 | R0, R3, R4 | Q1 (drive replacement) | no | 20…60
x | no | Primary current path | [9 empty] | 0
x | no | Primary current path | Primary contacts | [8 empty] | 0
x | no | Primary current path | Rotary joints | [8 empty] | 0
x | no | Primary current path | Flexible joints | [8 empty] | 0
x | no | Primary current path | Commutating contacts | [8 empty] | 0
x | no | Primary current path | Other | [8 empty] | 0
x | no | Kinematic chain (mechanical transmission elements between operating mechanism and making and breaking units) | [9 empty] | 0
x | no | Kinematic chain (mechanical transmission elements between operating mechanism and making and breaking units) | Pipes, beam (including screw connections) | [8 empty] | 0
x | no | Kinematic chain (mechanical transmission elements between operating mechanism and making and breaking units) | Bearing,(ball bearing, bush) | [8 empty] | 0
x | no | Kinematic chain (mechanical transmission elements between operating mechanism and making and breaking units) | Damping device (spring) | [8 empty] | 0
x | no | Kinematic chain (mechanical transmission elements between operating mechanism and making and breaking units) | interlock | [8 empty] | 0
x | no | Kinematic chain (mechanical transmission elements between operating mechanism and making and breaking units) | Base frame | [8 empty] | 0
x | no | Kinematic chain (mechanical transmission elements between operating mechanism and making and breaking units) | Drive insulators | [8 empty] | 0
x | no | Kinematic chain (mechanical transmission elements between operating mechanism and making and breaking units) | Other | [8 empty] | 0
x | no | Operating mechanism (earthed) | [9 empty] | 0
x | no | Operating mechanism (earthed) | Electrical motors | [8 empty] | 0
x | no | Operating mechanism (earthed) | Energy storage (accumulator, spring) | [8 empty] | 0
x | no | Operating mechanism (earthed) | Control elements (non-electrical) | [8 empty] | 0
x | no | Operating mechanism (earthed) | Actuator and damping device | [8 empty] | 0
x | no | Operating mechanism (earthed) | Mechanical transmission (when part of operating mechanism e.g.. gear) | [8 empty] | 0
x | no | Operating mechanism (earthed) | Other | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | [9 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Control circuits | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Auxiliary switches and associated drives | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Contactors | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Relays | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Heaters | [8 empty] | 0
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Thermostats
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Fuses
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Cables and terminal blocks
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Monitoring devices (including sensors)
x | no | Electrical control and auxiliary circuits (when part of DC / ES) | Other

## IT_MVT_CT_A
|  | Ageing Card for Magnetic Voltage Transformers and Current Transformers (including: optical instrument transformers; excluding: GIS equipment) |  | A0 - Electrical degradation A1 - - Loss of dielectric strength A2 - - Punctures A3 - - Burn out B0 - Mechanical degradation B1 - - Cracking B2 - - Local loss of glace B3 - - Deformation B4 - - Frost wedging B5 - - Erosion B6 - - Leakage of internal insulation C0 - Material degradation C1 - - Corrosion C2 - - Loss of hydrophobicity C3 - - Modification of gaskets characteristics D0 - Others (please specify) | F0 - Electrical stresses F1 - - Over voltages/currents F2 - - Lightning voltages/currents F3 - - Ferro resonance F4 - - Corona F5 - - Heat from arc G0 - Dielectric stress H0 - Mechanical stresses H1 - - Thermal stress I0 - Environmental influence I1 - - Rain I2 - - Moisture I3 - - Dust I4 - - UV radiation I5 - - Temperature I6 - - Wind J0 - Others | Mi0 - Minor Failure Modes Mi1 - - Leakage of insulating fluid Mi2 - - Loss of accuracy Mi3 - - Changes in dielectric functional characteristics Mi4 - - Other Ma0 - Major Failure Modes Ma1 - - External flashover Ma2 - - Internal burnout Ma3 - - Out of accuracy tolerances Ma4 - - False signals for protection and control system Ma5 - - Loss of electrical connections integrity in secondary Ma6 - - Damping circuit loss of function Ma7 - - Monitoring device loss of function Ma8 - - Other | R0 - Visual inspection R1 - Thermography R2 - UV inspection R3 - Pressure monitoring R4 - Capacitance testing R5 - Oil or gas analysis R6 - Ductor testing R7 - Winding resistance measurements R8 - Ratio testing R9 - Others | Q0 - Complete IT replacement Q1 - Component replacement Q2 - Insulating medium replacement (e.g. oil, gas) Q3 - Component repair Q4 - Other | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing, what failure modes has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the equipment life was the reported ageing phenomenon experienced? | no | 0
x | e.g. | Component in primary part | HV tank | B6 | I1, I5 | Mi1, Ma2 | R3 | Q0, Q4 |  | 25…30
x | no | Component in primary part | [9 empty] | 0
x | no | Component in primary part | HV tank | [8 empty] | 0
x | no | Component in primary part | HV primary terminal
x | no | Component in primary part | Insulator (porcelain) | [8 empty] | 0
x | no | Component in primary part | Insulator (composite)
x | no | Component in primary part | Insulator (resin)
x | no | Component in primary part | Earthed metal tank or enclosure | [8 empty] | 0
x | no | Component in primary part | Bushing (internal tube) | [8 empty] | 0
x | no | Component in primary part | Spacer or any other rigid HV internal insulation | [8 empty] | 0
x | no | Component in primary part | Main internal insulation (oil, paper) | [8 empty] | 0
x | no | Component in primary part | Main internal insulation (SF6)
x | no | Component in primary part | Main internal insulation (other, please specify)
x | no | Component in primary part | Primary winding | [8 empty] | 0
x | no | Component in primary part | Components for expansion control of insulation medium | [8 empty] | 0
x | no | Component in primary part | Components for pressure relieve of insulation medium
x | no | Component in primary part | Sealing (e.g. gaskets and O-rings) | [8 empty] | 0
x | no | Component in primary part | Primary part at optical IT (e.g. sensing device, polarizing element) | [8 empty] | 0
x | no | Component in primary part | Optical fibre in primary part of optical IT | [8 empty] | 0
x | no | Component in primary part | Part of component in primary part but unidentified | [8 empty] | 0
x | no | Internal component in secondary part | [9 empty] | 0
x | no | Internal component in secondary part | Secondary winding | [8 empty] | 0
x | no | Internal component in secondary part | Secondary winding insulation | [8 empty] | 0
x | no | Internal component in secondary part | Shielding of secondary winding | [8 empty] | 0
x | no | Internal component in secondary part | Internal earthing connections and bushings | [8 empty] | 0
x | no | Internal component in secondary part | Internal damping circuits components | [8 empty] | 0
x | no | Internal component in secondary part | Secondary reconnection taps | [8 empty] | 0
x | no | Internal component in secondary part | Optical device in optical IT (e.g. LED, SLD, photo-diode, polarizing element, sensing device) | [8 empty] | 0
x | no | Internal component in secondary part | Transmission optical fibre at optical IT | [8 empty] | 0
x | no | Internal component in secondary part | Electrical circuit at optical IT | [8 empty] | 0
x | no | External (air insulated) accessory | [9 empty] | 0
x | no | External (air insulated) accessory | Terminal board | [8 empty] | 0
x | no | External (air insulated) accessory | External earthing | [8 empty] | 0
x | no | External (air insulated) accessory | External LV cable connection | [8 empty] | 0
x | no | External (air insulated) accessory | Pressure (density) monitoring device | [8 empty] | 0
x | no | External (air insulated) accessory | Pipes and sealing for pressure (density) monitoring device | [8 empty] | 0
x | no | External (air insulated) accessory | High frequency equipment protection components | [8 empty] | 0
x | no | External (air insulated) accessory | Monitoring devices other than pressure and density (e.g. free gas detection monitoring, etc.) | [8 empty] | 0
x | no | External (air insulated) accessory | Any other accessory | [8 empty] | 0

## IT_CVT_A
|  | Ageing Card for Capacitive Voltage Transformer (excluding: GIS equipment) |  | A0 - Electrical degradation A1 - - Loss of dielectric strength A2 - - Punctures A3 - - Burn out B0 - Mechanical degradation B1 - - Cracking B2 - - Local loss of glace B3 - - Deformation B4 - - Frost wedging B5 - - Erosion B6 - - Leakage of internal insulation C0 - Material degradation C1 - - Corrosion C2 - - Loss of hydrophobicity C3 - - Modification of gaskets characteristics D0 - Others (please specify) | F0 - Electrical stresses F1 - - Over voltages/currents F2 - - Lightning voltages/currents F3 - - Ferro resonance F4 - - Corona F5 - - Heat from arc G0 - Dielectric stress H0 - Mechanical stresses H1 - - Thermal stress I0 - Environmental influence I1 - - Rain I2 - - Moisture I3 - - Dust I4 - - UV radiation I5 - - Temperature I6 - - Wind J0 - Others | Mi0 - Minor Failure Modes Mi1 - - Leakage of insulating fluid Mi2 - - Loss of accuracy Mi3 - - Changes in dielectric functional characteristics Mi4 - - Other Ma0 - Major Failure Modes Ma1 - - External flashover Ma2 - - Internal burnout Ma3 - - Out of accuracy tolerances Ma4 - - False signals for protection and control system Ma5 - - Loss of electrical connections integrity in secondary Ma6 - - Damping circuit loss of function Ma7 - - Monitoring device loss of function Ma8 - - Other | R0 - Visual inspection R1 - Thermography R2 - UV inspection R3 - Pressure monitoring R4 - Capacitance testing R5 - Oil or gas analysis R6 - Ductor testing R7 - Winding resistance measurements R8 - Ratio testing R9 - Others | Q0 - Complete IT replacement Q1 - Component replacement Q2 - Insulating medium replacement (e.g. oil, gas) Q3 - Component repair Q4 - Other | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing, what failure modes has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the equipment life was the reported ageing phenomenon experienced? | no | 0
x | e.g. | Component in primary part | HV tank | B6 | I1, I5 | Mi1, Ma2 | R0 | Q0, Q4 |  | 25…30
x | no | Component in primary part | [9 empty] | 0
x | no | Component in primary part | HV tank | [8 empty] | 0
x | no | Component in primary part | HV primary terminal
x | no | Component in primary part | Insulator (porcelain) | [8 empty] | 0
x | no | Component in primary part | Insulator (composite)
x | no | Component in primary part | Insulator (resin)
x | no | Component in primary part | Earthed metal tank or enclosure | [8 empty] | 0
x | no | Component in primary part | Bushing (internal tube) | [8 empty] | 0
x | no | Component in primary part | Spacer or any other rigid HV internal insulation | [8 empty] | 0
x | no | Component in primary part | Main internal insulation (oil, paper) | [8 empty] | 0
x | no | Component in primary part | Main internal insulation (SF6)
x | no | Component in primary part | Main internal insulation (other, please specify)
x | no | Component in primary part | Primary winding | [8 empty] | 0
x | no | Component in primary part | Capacitors in CVT | [8 empty] | 0
x | no | Component in primary part | Components for expansion control of insulation medium | [8 empty] | 0
x | no | Component in primary part | Components for pressure relieve of insulation medium
x | no | Component in primary part | Sealing (e.g. gaskets and O-rings) | [8 empty] | 0
x | no | Component in primary part | Part of component in primary part but unidentified | [8 empty] | 0
x | no | Internal component in secondary part | [9 empty] | 0
x | no | Internal component in secondary part | Secondary winding | [8 empty] | 0
x | no | Internal component in secondary part | Secondary winding insulation | [8 empty] | 0
x | no | Internal component in secondary part | Shielding of secondary winding | [8 empty] | 0
x | no | Internal component in secondary part | Internal earthing connections and bushings | [8 empty] | 0
x | no | Internal component in secondary part | Internal damping circuits components | [8 empty] | 0
x | no | Internal component in secondary part | Secondary reconnection taps | [8 empty] | 0
x | no | External (air insulated) accessory | [9 empty] | 0
x | no | External (air insulated) accessory | Terminal board | [8 empty] | 0
x | no | External (air insulated) accessory | External earthing | [8 empty] | 0
x | no | External (air insulated) accessory | External LV cable connection | [8 empty] | 0
x | no | External (air insulated) accessory | Pressure (density) monitoring device | [8 empty] | 0
x | no | External (air insulated) accessory | Pipes and sealing for pressure (density) monitoring device | [8 empty] | 0
x | no | External (air insulated) accessory | High frequency equipment protection components | [8 empty] | 0
x | no | External (air insulated) accessory | Monitoring devices other than pressure and density (e.g. free gas detection monitoring, etc.) | [8 empty] | 0
x | no | External (air insulated) accessory | Any other accessory | [8 empty] | 0

## IT_CCVT_A
|  | Ageing Card for Combined Current and Voltage Transformers (excluding: GIS equipment) |  | A0 - Electrical degradation A1 - - Loss of dielectric strength A2 - - Punctures A3 - - Burn out B0 - Mechanical degradation B1 - - Cracking B2 - - Local loss of glace B3 - - Deformation B4 - - Frost wedging B5 - - Erosion B6 - - Leakage of internal insulation C0 - Material degradation C1 - - Corrosion C2 - - Loss of hydrophobicity C3 - - Modification of gaskets characteristics D0 - Others (please specify) | F0 - Electrical stresses F1 - - Over voltages/currents F2 - - Lightning voltages/currents F3 - - Ferro resonance F4 - - Corona F5 - - Heat from arc G0 - Dielectric stress H0 - Mechanical stresses H1 - - Thermal stress I0 - Environmental influence I1 - - Rain I2 - - Moisture I3 - - Dust I4 - - UV radiation I5 - - Temperature I6 - - Wind J0 - Others | Mi0 - Minor Failure Modes Mi1 - - Leakage of insulating fluid Mi2 - - Loss of accuracy Mi3 - - Changes in dielectric functional characteristics Mi4 - - Other Ma0 - Major Failure Modes Ma1 - - External flashover Ma2 - - Internal burnout Ma3 - - Out of accuracy tolerances Ma4 - - False signals for protection and control system Ma5 - - Loss of electrical connections integrity in secondary Ma6 - - Damping circuit loss of function Ma7 - - Monitoring device loss of function Ma8 - - Other | R0 - Visual inspection R1 - Thermography R2 - UV inspection R3 - Pressure monitoring R4 - Capacitance testing R5 - Oil or gas analysis R6 - Ductor testing R7 - Winding resistance measurements R8 - Ratio testing R9 - Others | Q0 - Complete IT replacement Q1 - Component replacement Q2 - Insulating medium replacement (e.g. oil, gas) Q3 - Component repair Q4 - Other | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing, what failure modes has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the equipment life was the reported ageing phenomenon experienced? | no | 0
x | e.g. | Component in primary part | HV tank | B6 | I1, I5 | Mi1, Ma2 | R0 | Q0, Q4 |  | 25…30
x | no | Component in primary part | [9 empty] | 0
x | no | Component in primary part | HV tank | [8 empty] | 0
x | no | Component in primary part | HV primary terminal
x | no | Component in primary part | Insulator (porcelain) | [8 empty] | 0
x | no | Component in primary part | Insulator (composite)
x | no | Component in primary part | Insulator (resin)
x | no | Component in primary part | Earthed metal tank or enclosure | [8 empty] | 0
x | no | Component in primary part | Bushing (internal tube) | [8 empty] | 0
x | no | Component in primary part | Spacer or any other rigid HV internal insulation | [8 empty] | 0
x | no | Component in primary part | Main internal insulation (oil, paper) | [8 empty] | 0
x | no | Component in primary part | Main internal insulation (SF6)
x | no | Component in primary part | Main internal insulation (other, please specify)
x | no | Component in primary part | Primary winding | [8 empty] | 0
x | no | Component in primary part | Capacitors in CVT | [8 empty] | 0
x | no | Component in primary part | Components for expansion control of insulation medium | [8 empty] | 0
x | no | Component in primary part | Components for pressure relieve of insulation medium
x | no | Component in primary part | Sealing (e.g. gaskets and O-rings) | [8 empty] | 0
x | no | Component in primary part | Part of component in primary part but unidentified | [8 empty] | 0
x | no | Internal component in secondary part | [9 empty] | 0
x | no | Internal component in secondary part | Secondary winding | [8 empty] | 0
x | no | Internal component in secondary part | Secondary winding insulation | [8 empty] | 0
x | no | Internal component in secondary part | Shielding of secondary winding | [8 empty] | 0
x | no | Internal component in secondary part | Internal earthing connections and bushings | [8 empty] | 0
x | no | Internal component in secondary part | Internal damping circuits components | [8 empty] | 0
x | no | Internal component in secondary part | Secondary reconnection taps | [8 empty] | 0
x | no | External (air insulated) accessory | [9 empty] | 0
x | no | External (air insulated) accessory | Terminal board | [8 empty] | 0
x | no | External (air insulated) accessory | External earthing | [8 empty] | 0
x | no | External (air insulated) accessory | External LV cable connection | [8 empty] | 0
x | no | External (air insulated) accessory | Pressure (density) monitoring device | [8 empty] | 0
x | no | External (air insulated) accessory | Pipes and sealing for pressure (density) monitoring device | [8 empty] | 0
x | no | External (air insulated) accessory | High frequency equipment protection components | [8 empty] | 0
x | no | External (air insulated) accessory | Monitoring devices other than pressure and density (e.g. free gas detection monitoring, etc.) | [8 empty] | 0
x | no | External (air insulated) accessory | Any other accessory | [8 empty] | 0

## SA_A
|  | Ageing Card for Surge Arresters |  |  | A0 - Electrical degradation A1 - - - Decreasing of resistivity A2 - - - Increase of power loss A3 - - - Loss of dielectric strength A4 - - - Erosion A5 - - - Electrical treeing A6 - - - Change of resistance B0 - Mechanical degradation B1 - - - Deformation B2 - - - Cracking B3 - - - Fatigue B4 - - - Relaxation B5 - - - Loosening of loading force C0 - Material degradation C1 - - - Corrosion C2 - - - Degradation of resin D0 - Others | F0 - Electrical stresses F1 - - - Lightning voltages/currents F2 - - - Switching voltages/currents G0 - Dielectric stress H0 - Mechanical stresses H1 - - - Pressure H2 - - -Thermal stress I1 - Environmental influence I2 - - - Rain I3 - - - Moisture I4 - - - Dust I5 - - - UV radiation I6 - - - Temperature J0 - Others | Mi0 - Minor failure modes Mi1 - Change in electrical functional characteristics Mi2 - Moisture ingress Mi3 - Gas leakage Mi4 - Overheating Mi5 - Tracking (creepage path) Mi6 - Increased contact resistance Mi7 - Higher losses Mi8 - Loss of gap grading Mi9 - Others Ma0 - Major failure modes Ma1 - Insulation breakdown Ma2 - Internal breakdown Ma3 - Mechanical damage Ma4 - Flash over Ma5 - Others | R0 - Visual inspection R1 - Thermographic inspection R2 - Leakage current measurement R3 - Arrestor counter R4 - Flashover voltage test R5 - PD Detection R6 - Corona measurement R7 - Tightness test | Q0 - Complete unit replacement Q1 - Component replacement Q2 - Surface Treatment Q3 - Others | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | Optional subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing, what failure modes (of minor failures) has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the equipment life was the reported ageing phenomenon experienced | no | 0
| e.g. | Active part | Active part MO | MO resistor | A1 | F1, F2 | Mi0 | R1 | Q0 | no | 30…40
x | no | Active part | Active part MO | [9 empty] | 0
x | no | Active part | Active part MO | MO resistor | [8 empty] | 0
x | no | Active part | Active part MO | Copper Sheet | [8 empty] | 0
x | no | Active part | Active part MO | Spacers | [8 empty] | 0
x | no | Active part | Active part MO | Fibre Glass Loops / Rods | [8 empty] | 0
x | no | Active part | Active part MO | Spring (Tube design) | [8 empty] | 0
x | no | Active part | Active part Gapped SiC | [9 empty] | 0
x | no | Active part | Active part Gapped SiC | Grading resistor | [8 empty] | 0
x | no | Active part | Active part Gapped SiC | Spark gap | [8 empty] | 0
x | no | Enclosure | Insulation | [9 empty] | 0
x | no | Enclosure | Insulation | Porcelain Enclosure | [8 empty] | 0
x | no | Enclosure | Insulation | Polymer Enclosure | [8 empty] | 0
x | no | Enclosure | Insulation | Metal Enclosure (GIS) | [8 empty] | 0
x | no | Enclosure | Sealing | [9 empty] | 0
x | no | Enclosure | Sealing | Sealing parts | [8 empty] | 0
x | no | Enclosure | Sealing | Pressure relief diaphragm | [8 empty] | 0
x | no | Enclosure | Moisture absorber | [9 empty] | 0
x | no | Enclosure | Moisture absorber | Desiccant bag | [8 empty] | 0
x | no | Enclosure | Others | [9 empty] | 0
x | no | Enclosure | Others | Others | [8 empty] | 0
x | no | Accessories | Stress grading (over 200 kV) | [9 empty] | 0
x | no | Accessories | Stress grading (over 200 kV) | Grading Ring Struts | [8 empty] | 0

## CAP_A
|  | Ageing Card for Shunt Capacitors (excluding: grading capacitors of CB) |  |  | A0 - Electrical degradation A1 - - Loss of dielectric strength A2 - - Overheating B0 - Mechanical degradation B1 - - Cracking C0 - Material degradation C1 - - Oxidation C2 - - Corrosion C3 - - Loosing elasticity D0 - others (please specify) | F0 - Electrical stresses F1 - - - Lightning voltages/currents F2 - - - Corona F3 - - - Harmonics G0 - Dielectric stress H0 - Mechanical stresses H1 - - -Thermal stress I0 - Environmental influence I1 - - - Rain I2 - - - Moisture I3 - - - Dust I4 - - - UV radiation I5 - - - Temperature J0 - Others | Ma1 - Does not provide rated capacitance Ma2 - Does not hold all insulating media | R0 - Visual inspection R1- Acoustic measurements R2 - Thermography R3 - Hydrophobicity measurements R4 - Multispectral cameras R5 - Corona measurement | Q1 - Replacement Q2 - Repair Q3 - Washing Q4 - Grease or silicone coating | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | Optional subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing of shunt capacitors, what failure modes has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the equipment life was the reported ageing phenomenon experienced | no | 0
| e.g. | Enclosure | Tank | Container | C2 | I0 |  | R0 | Q1
x | no | Internal component | Active pack | [9 empty] | 0
x | no | Internal component | Active pack | Winding (capacitor element) | [8 empty] | 0
x | no | Internal component | Active pack | Insulating support | [8 empty] | 0
x | no | Internal component | External insulation | [9 empty] | 0
x | no | Internal component | External insulation | External insulation | [8 empty] | 0
x | no | Internal component | Conductor | [9 empty] | 0
x | no | Internal component | Conductor | Copper wire | [8 empty] | 0
x | no | Enclosure | Tank | [9 empty] | 0
x | no | Enclosure | Tank | Container | [8 empty] | 0
x | no | Enclosure | Tank | Painting | [8 empty] | 0
x | no | Terminal | Bushing | [9 empty] | 0
x | no | Terminal | Bushing | Top and bottom joint | [8 empty] | 0
x | no | Terminal | Bushing | Conductor | [8 empty] | 0
x | no | Terminal | Bushing | Insulator | [8 empty] | 0
x | no | Terminal | End terminal, clamping unit | Top and bottom clamp | [8 empty] | 0
x | no | Bank construction | Interconnection | [9 empty] | 0
x | no | Bank construction | Interconnection | Cable and/or wire, clasp | [8 empty] | 0

## PI_A
|  | Ageing Card for Post Insulators |  |  | A0 - Electrical degradation A1 - - Loss of dielectric strength A2 - - Punctures B0 - Mechanical degradation B1 - - Cracking B2 - - Local loss of glaze B3 - - Deformation B4 - - Frost wedging B5 - - Erosion C0 - Material degradation C1 - - Brittle fracture C2 - - Corrosion C3 - - Loss of hydrophobicity D0 - Others (please specify) | F0 - Electrical stresses F1 - - - Lightning voltages/currents F2 - - - Corona F3 - - - Heat from arc G0 - Dielectric stress H0 - Mechanical stresses H1 - - -Thermal stress I0 - Environmental influence I1 - - - Rain I2 - - - Moisture I3 - - - Dust I4 - - - UV radiation I5 - - - Temperature J0 - Others | Ma1 - Does not provide electrical insulation to earth Ma2 - Does not provide mechanical support | R0 - Visual inspection R1- Acoustic measurements R2 - Thermography R3 - Hydrophobicity measurements R4 - Multispectral cameras R5 - Corona measurement | Q1 - Replacement Q2 - Repair Q3 - Washing Q4 - Grease or silicone coating | 1 - Does your organisation intend to change the detection/ mitigation? 2 - Does your organisation intend to introduce new ? 3 - Does your organisation intend to discontinue any of the existing techniques ? | 0…5 5…10 10…15 15…20 25…30 30…40 40…50 50…60 60…… | yes | has the form been filled out?
Original row | Choice | Component | Subcomponent | Optional subcomponent | In your organisation what ageing phenomenon have you experienced? | For your organisation which of the following factors have influenced ageing phenomenon? | As a consequence of ageing of post insulators, what failure modes has your organisation experienced? | What detection techniques were/are used by your organisation to detect the reported ageing phenomenon? | What mitigation techniques were/are used by your organisation to mitigate against the reported ageing phenomenon? | Please answer with free-text to the questions above. | Based on your experience at what stage of the equipment life was the reported ageing phenomenon experienced | no | 0
x | e.g. | Porcelain post insulator | Insulating unit | Insulating body | B4 | I0, J0 |  | R0, R1 | Q1
x | no | Porcelain post insulator | Insulating unit | [9 empty] | 0
| no | Porcelain post insulator | Insulating unit | Insulating body | [8 empty] | 0
x | no | Porcelain post insulator | Insulating unit | Glaze | [8 empty] | 0
x | no | Porcelain post insulator | End fitting | [9 empty] | 0
x | no | Porcelain post insulator | End fitting | Flange | [8 empty] | 0
x | no | Porcelain post insulator | End fitting | Cement | [8 empty] | 0
x | no | Composite post insulator | Insulating unit | [9 empty] | 0
x | no | Composite post insulator | Insulating unit | Mechanically supporting structure | [8 empty] | 0
x | no | Composite post insulator | Insulating unit | Housing | [8 empty] | 0
x | no | Composite post insulator | Insulating unit | Interior (for hollow insulators) | [8 empty] | 0
x | no | Composite post insulator | End fitting | [9 empty] | 0
x | no | Composite post insulator | End fitting | Flange | [8 empty] | 0
x | no | Composite post insulator | End fitting | Attachment | [8 empty] | 0

## Def
| Definition |  | Definition | Cestina | English | French | German | Japanese | Norsk | Polski | Spanish | Croatian | Italian | Romanian | CB | DS | IT | CAP | PI | SA
0.1 | Navigation | 0.1 | Navigation
- Please use only the navigation buttons provided in this document. Do not use the Microsoft Windows functionalities to swap between the windows.
- If you need help please choose the button with question mark "?".
- In order to leave this help document choose the button "return"
| - You will find the pages to be filled out in the "Main Menu". If your resolution is very low, you may have to scroll down in order to see the menu. |  | - You will find the pages to be filled out in the "main men". If your resolution is very low, you may have to scroll down in order to see the menu.
| - You may go back to "Main Menu" by pressing the button "Back to Main Menu". Your competed data remain unchanged. However, please do not forget to save your work using typical Excell functions. |  | - You may go back to "Main Manu" by pressing the button "Back to main menu". Your work will remain unchanged. However, please do not forget to press the "SAVE" button.
0,11 | Saving
- Saving instructions: Since many persons may participate in filling out of the survey, it is important to save their work in proper manner. For this reason for saving only the button "Extract and Save" should be used. Using it a specific file name will be generated.
0.1 | Filling the general information cards | 0.1 | Filling the general information cards
| 1. Fill only the cells with white background |  | 1. Fill only the cells with white background
| 2. Some cells have dependencies. The cells you need to fill up will be marked with white background. |  | 2. Some cells have dependencies. The cells you need to fill up will be marked with white background.
0.2 | Filling the ageing cards | 0.2 | Filling the ageing cards
| 1. Select the components you would like to share your experience by choosing "yes" in Column B |  | 1. Select the components you would like to share your experience by choosing "yes" in Column B (you may also type yes or no it is in some cases faster)
| 2. Filter your selection by applying the filter in Cell B2 (upside down triangle). Select only "yes". You will have to repeat this every time you have changed the selection. |  | 2. Filter your selection by applying the filter in Cell B2 (upside down triangle). Select only "yes". You will have to repeat this every time you have changed the selection.
| 3. Choose only one ageing phenomenon out of the list and write in the cell the code (e.g. A1) If you do not exactly know what was the phenomenon, you may also choose the main group one level higher (e.g. A0, B0, etc.) |  | 3. Choose only one ageing phenomenon out of the list and write in the cell the code (e.g. A1) If you do not exactly know what was the phenomenon you may also choose the thick group (e.g. A0)
| 3a. If you would like to add more than one phenomenon to the component, please select the cell with component you would like to duplicate, press button "Add row". Now you can fill out the second ageing phenomenon |  | 3a. If you would like to add more than one phenomenon to the component, please select the cell with component you would like to duplicate, press button "Add row". Now you can fill out the second ageing phenomenon
| 3b. In order to remove the added row, choose the row and press button "Delete Row". NOTE: you may remove rows, which were only added by yourself. |  | 3b. In order to remove the added row, choose the row and press button "Delete Row". You may remove rows, which were only added by yourself.
| 4. Fill out the column which consists of the "factors influencing the ageing". You may simply write down the codes out of the list given in cell "G1" or type your own text. You may choose multiple factors. |  | 4. Fill out the factors influencing the ageing. You may simply write down the codes out of the list given in cell G1 or type your own text. You may choose multiple factors.
| 5. Fill out the column which consists of the "failure mode". You may simply write down the codes out of the list given in cell "H1" or type your own text. You may choose multiple modes. |  | 5. Fill out the failure mode. You may simply write down the codes out of the list given in cell H1 or type your own text. You may choose multiple modes.
| 6. Fill out the column which consists of the "detection techniques". You may simply write down the codes out of the list given in cell "I1" or type your own text. You may choose multiple techniques. |  | 6. Fill out the detection techniques. You may simply write down the codes out of the list given in cell I1 or type your own text. You may choose multiple techniques.
| 7. Fill out the column which consists of the "mitigation techniques. You may simply write down the codes out of the list given in cell "I26" or type your own text. You may choose multiple techniques |  | 7. Fill out the mitigation techniques. You may simply write down the codes out of the list given in cell I26 or type your own text. You may choose multiple techniques
| 8. Answer the questions in cell "K1" by typing a free text |  | 8. Answer the questions in cell K1 by typing a free text
| 9. Choose at what age according to your experience, the component fails. |  | 9. Choose at what age according to your experience, the component will fail.
| OTHER REMARKS: * If you cannot scroll the window, please remove the option "Freeze panes" in menu view * If you do not know what to fill out, please leave the cell without input. |  | OTHER REMARKS: * If you cannot scroll the window, please remove the option "Freeze panes" in menu view * If you do not know what to fill out, please leave the cell without input.
1.3 | Rated voltage classes | 1.3 | Rated voltage classes | Napetova trida | Rated voltage classes | Classes de tension assignée | Klasse der Bemessungs-Spannung | 定格電圧分類 | Merkespenninger | Klasy napięcia znamionowego | Clases de tensión asignada | Nazivna naponska klasa | Rated voltage classes | Clasele de tensiune nominala | X | X | X | X | X | X
| Rated voltage of the equipment. (The rated voltage indicates the upper limit of the highest voltage of systems for which the switchgear and control gear is intended / the nameplate value) |  | Rated voltage of the equipment. (The rated voltage indicates the upper limit of the highest voltage of systems for which the switchgear and controlgear is intended / the nameplate value) | Jmenovite napeti zarizeni (= nejvyssi provozovaci napeti site, pro nez je zarizeni urceno /stitkova hodnota zarizeni) | Rated voltage of the equipment. (The rated voltage indicates the upper limit of the highest voltage of systems for which the switchgear and controlgear is intended / the nameplate value) | Tension assignée de l'équipement (la tension assignée indique la limite supérieure de la tension la plus élevée du système pour lesquels le matériel est prévu/ valeur indiquée sur la plaque signalétique) | Bemessungs-Spannung des Gerätes (Die Bemessungsspannung indiziert das obere Limit der Systemspannung für welche das Schaltgerät/Steuerungsgerät ausgelegt ist / Angabe auf dem Leistungsschild) | 機器の定格電圧（定格電圧は、その開閉機器のシステム最高電圧や銘板記載の値を意味します。） | Utstyrets merkespenning. (Merkespenningen angir den øvre grense for den høyeste spenningen til systemer bryteren og kontrollutstyrer er tenkt for / merkeskiltverdien) | Napięcie znamionowe aparatu (The rated voltage indicates the upper limit of the highest voltage of systems for which the switchgear and controlgear is intended / the nameplate value) | Clase de tensión asignada del equipo (La tensión asignada indica el límite superior de la tensión más alta de los sistemas para el cual la aparamenta esta prevista / valor de la placa) | Nazivni napon opreme (Nazivni napon pokazuje gornju granicu najvišeg pogonskog napona za koji je postrojenje namjenjeno / podatak na natpisnoj pločici) | Rated voltage of the equipment. (The rated voltage indicates the upper limit of the highest voltage of systems for which the switchgear and controlgear is intended / the nameplate value) | Tensiunea nominala a echipamentului. (Tensiunea nominala este limita superioara a celei mai inalte tensiuni a sistemului pentru care este proiectat echipamentul de comutatie si control / valoarea de pe placuta.) | X | X | X | X | X | X
| Class 1 : 60<= Un<100 kV |  | Class 1 : 60<= Un<100 kV | Trida 1 : 60<= Un<100 kV | Class 1 : 60<= Un<100 kV | Classe 1 : 60<= Un<100 kV | Klasse 1 : 60<= Un<100 kV | クラス 1 : 60<= Un<100 kV | Klasse 1 : 60<= Un<100 kV | Klasa 1 : 60<= Un<100 kV | Clase 1: 60<= Un<100 kV | Klasa 1 : 60<= Un<100 kV | Class 1 : 60<= Un<100 kV | Clasa 1 : 60<= Un<100 kV | X | X | X | X | X | X
| Class 2 : 100<= Un<200 kV |  | Class 2 : 100<= Un<200 kV | Trida 2 : 100<= Un<200 kV | Class 2 : 100<= Un<200 kV | Classe 2 : 100<= Un<200 kV | Klasse 2 : 100<= Un<200 kV | クラス 2 : 100<= Un<200 kV | Klasse 2 : 100<= Un<200 kV | Klasa 2 : 100<= Un<200 kV | Clase 2: 100<= Un<200 kV | Klasa 2 : 100<= Un<200 kV | Class 2 : 100<= Un<200 kV | Clasa 2 : 100<= Un<200 kV | X | X | X | X | X | X
| Class 3 : 200<= Un<300 kV |  | Class 3 : 200<= Un<300 kV | Trida 3 : 200<= Un<300 kV | Class 3 : 200<= Un<300 kV | Classe 3 : 200<= Un<300 kV | Klasse 3 : 200<= Un<300 kV | クラス 3 : 200<= Un<300 kV | Klasse 3 : 200<= Un<300 kV | Klasa 3 : 200<= Un<300 kV | Clase 3: 200<= Un<300 kV | Klasa 3 : 200<= Un<300 kV | Class 3 : 200<= Un<300 kV | Clasa 3 : 200<= Un<300 kV | X | X | X | X | X | X
| Class 4 : 300<= Un<500 kV |  | Class 4 : 300<= Un<500 kV | Trida 4 : 300<= Un<500 kV | Class 4 : 300<= Un<500 kV | Classe 4 : 300<= Un<500 kV | Klasse 4 : 300<= Un<500 kV | クラス 4 : 300<= Un<500 kV | Klasse 4 : 300<= Un<500 kV | Klasa 4 : 300<= Un<500 kV | Clase 4: 300<= Un<500 kV | Klasa 4 : 300<= Un<500 kV | Class 4 : 300<= Un<500 kV | Clasa 4 : 300<= Un<500 kV | X | X | X | X | X | X
| Class 5 : 500<= Un<700 kV |  | Class 5 : 500<= Un<700 kV | Trida 5 : 500<= Un<700 kV | Class 5 : 500<= Un<700 kV | Classe 5 : 500<= Un<700 kV | Klasse 5 : 500<= Un<700 kV | クラス 5 : 500<= Un<700 kV | Klasse 5 : 500<= Un<700 kV | Klasa 5 : 500<= Un<700 kV | Clase 5: 500<= Un<700 kV | Klasa 5 : 500<= Un<700 kV | Class 5 : 500<= Un<700 kV | Clasa 5 : 500<= Un<700 kV | X | X | X | X | X | X
| Class 6 : Un>=700 kV |  | Class 6 : Un>=700 kV | Trida 6 : Un>=700 kV | Class 6 : Un>=700 kV | Classe 6 : Un>=700 kV | Klasse 6 : Un>=700 kV | クラス 6 : Un>=700 kV | Klasse 6 : Un>=700 kV | Klasa 6 : Un>=700 kV | Clase 6: Un>700 kV | Klasa 6 : Un>=700 kV | Class 6 : Un>=700 kV | Clasa 6 : Un>=700 kV | X | X | X | X | X | X
| Note for utilities in Japan: |  | Note for utilities in Japan: | Poznamka pro Japonsko | Note for utilities in Japan: | Note pour le Japon : | Anmerkung für Japan: | ＊（注）日本ユーザーへの特記事項 | NB! Japanske everk: | Uwaga dla przedsiębiorstw w Japonii: | Nota para las compañias de Japón: | Napomena za korisnike u Japanu: | Note for utilities in Japan: | Nota pentru utilitatile din Japonia: | X | X | X | X | X | X
| The voltage class 2 includes the JEC rated voltage level of 204 kV. |  | The voltage class 2 includes the JEC rated voltage level of 204 kV. | Napetova trida 2 obsahuje i zarizeni JEC s jm. napetim 204 kV. | The voltage class 2 includes the JEC rated voltage level of 204 kV. | La classe 2 de tension inclut le niveau de tension assignée par JEC de 204kV | Die Klasse 2 beinhaltet den JEC Bemessungs-Spannungslevel 204kV | 定格電圧クラス 2 は、JEC規定の204kVクラスを含みます。 | Spenningsklasse 2 inkluderer JEC merkespenning 204 kV | Klasa 2 napięcia obejmuje znamionowy poziom napięcia 204 zgodny z JEC | La clase de tensión 2, incluye el nivel de tensión 204 kV | Naponska klasa 2 uključuje JEC nazivni napon 204 kV | The voltage class 2 includes the JEC rated voltage level of 204 kV. | Clasa de tensiune nominala 2 include nivelul de tensiune 204kV. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.4 | AIS | 1.4 | AIS | Konvencni rozvodne zarizeni (AIS) | AIS | AIS | AIS | AIS | AIS | AIS | AIS | AIS | AIS | AIS | X | X | X | X | X | X
| Air Insulated Switchgear |  | Air Insulated Switchgear | Konvencni (vzduchem izolovane) rozvodne zarizeni (AIS) | Air Insulated Switchgear | Isolé dans l'air | Luftisolierte Schaltanlage | 気中絶縁開閉装置 | Luftisolerte anlegg | Rozdzielnica (Rozdzielnia) w Izolacji Powietrznej | Aparamenta de aislamiento aire | Zrakom izolirano postrojenje | Air Insulated Switchgear | Echipament de comutatie (aparataj electric) izolat in aer (Air Insulated Switchgear) | X | X | X | X | X | X
| Switchgear in the bays of which are fully made from AIS technology components. |  | Switchgear in the bays of which are fully made from AIS technology components. | je rozvodne zarizeni, jehoz pole jsou vyrobena zcela z komponentu technologie s izolaci vzduchem. | Switchgear in the bays of which are fully made from AIS technology components. | Appareillage d'une travée dont tous les composants sont entièrement réalisés en technologie AIS. | Schaltanlage, die nur aus luftisolierten Komponenten besteht | 気中絶縁技術に基づいて製作された機器を適用した回線の開閉装置。 | Brytere i felt som er laget av luftisolerte komponenter. | Rozdzielnia której pola są całkowicie wykonane z elementów w technologii AIS | Aparamenta totalmente construida por componentes de tecnología convencional. | Postrojenje čija su sva polja napravljena od komponenata AIS tehnologije | Switchgear in the bays of which are fully made from AIS technology components. | Echipament de comutatie in celulele care sunt in intregime formate din componente in tehnologie AIS. | X | X | X | X | X | X
| Note 1: AIS technology components are characterized by external air insulation, internal air, SF6, liquid or solid insulation, and by live porcelain or composite insulators or no enclosure. |  | Note 1: AIS technology components are characterized by external air insulation, internal air, SF6, liquid or solid insulation, and by live porcelain or composite insulators or no enclosure. | Pozn. 1 : Komponenty technologie s izolaci vzduchem jsou charakterizovany vnejsi izolaci tvorenou vzduchem a vnitrni izolaci tvorenou vzduchem, SF6, pevnou nebo kapalnou izolaci a porcelanovymi nebo kompozitnimi izolatory pod napetim nebo zadnymi pouzdry | Note 1: AIS technology components are characterized by external air insulation, internal air, SF6, liquid or solid insulation, and by live porcelain or composite insulators or no enclosure. | Note 1 : Les composants de technologie d'AIS sont caractérisés par l'isolation externe dans l'air, en interne, le SF6 ou un isolant liquide ou solide , et par des enveloppes en porcelaine ou en matériaux isolants composites ou pas d'enveloppe. | Anmerkung 1:Komponenten in AIS Technologie weisen als äußere Isolation Luft, als innere Isolation Luft oder SF6 oder Flüssig- oder Feststoffe auf. Ferner haben sie Isolatoren aus Porzellan, Verbundwerkstoffen oder gar kein Gehäuse. | 注 1: 気中絶縁技術に基づいて製作された機器とは、充電部外部が気中絶縁（内部は空気、SF6ガス、液体、気体などの絶縁媒体）の機器または、磁器碍管、複合碍管や接地された金属容器を使用していない機器を意味します。 | Note 1: AIS komponenter er karakterisert ved at de har luft som utvendig isolasjon og innvendig luft, SF6, væske eller fast isolasjon, og ved at de har porselen eller komposittisolator og ingen kapsling. | Uwaga 1: Elementy techonologii AIS charakteryzują się zewnętrzną izolacją powietrzną, wewnętrzną izolacją powietrzną, SF6, ciekłą, stałą, i izolatorami porcelanowymi lub kompozytowymi między częściami pod napięciem lub brakiem obudowy. | Nota 1: Componentes de tecnología AIS están caracterizado por aislamiento externo de aire, interno de aire, SF6, liquido o sólido y porcelana viva, aisladores de composite o sin envolvente. | Napomena 1: AIS komponente su karakterizirane s vanjskom izolacijom zrak, unutrašnjom izolacijom zrak, SF6, tekućina ili kruta izolacija, sa porculanskim ili kompozitnim izolatorima i sa ili bez kučišta | Note 1: AIS technology components are characterized by external air insulation, internal air, SF6, liquid or solid insulation, and by live porcelain or composite insulators or no enclosure. | Nota 1: Componentele in tehnologia AIS sunt caracterizate prin izolatia exterioara in aer, interioara in aer, SF6, izolatie lichida sau solida si prin portelan sau izolatori compozit sau fara carcasa. | X | X | X | X | X | X
| Note 2: In hybrid switchgear (switchgear the bays of which are made from a mix of GIS and AIS technology components), please refer to AIS or GIS in dependence of specific design of the referred component. |  | Note 2: In hybrid switchgear (switchgear the bays of which are made from a mix of GIS and AIS technology components), please refer to AIS or GIS in dependence of specific design of the referred component. | Pozn. 2 : V hybridnich rozvodnych zarizenich (zarizenich, jejichz pole jsou tvorena z komponentu technologie s izolaci vzduchem a z komponentu zapouzdrene technologie), prosim, vztahnete odpoved ke konvecnimu (AIS) nebo zapouzdrenemu (ZRZ) rozvodnemu zarizeni v zavislosti na konstrukci komponenty, o niz referujete. | Note 2: In hybrid switchgear (switchgear the bays of which are made from a mix of GIS and AIS technology components), please refer to AIS or GIS in dependence of specific design of the referred component. | Note 2 : Dans l'appareillage hybride (la travée est constituée d'un mélange de composants de technologie GIS et AIS), se référer SVP aux définitions AIS et GIS en fonction de la conception spécifique du composant considéré. | Anmerkung 2: Bei Hybridanlagen (Anlagen bei denen die Felder aus einem Mix von Komponenten in AIS- oder GIS-Technologie verwendet werden) beziehen Sie sich bitte je nach Art der betrachteten Komponente auf GIS oder AIS. | 注 2 : H-GIS機器 (GIS機器とAIS機器が複合化された回線の機器)に関しては、対象機器の構造によってGISかAISを選択して下さい。 | Note 2 : I hybride bryteranlegg (brytere i felt bestående av en kombinasjon av GIS og AIS teknologi), avgjør designen for den aktuelle komponenten om dette faller under GIS eller AIS teknologi. Hybride anlegg er svært sjeldne i Norge. | Uwaga 2: W przypadku rozdzielnic hybrydowych ( rozdzielnic których pola są wykonane z elementów w technologii GIS i AIS), prosimy odnosić się do AIS lub GIS w zależności od określonego rozwiązania stosownego elementu. | Nota 2 : En la aparamenta híbrida (la aparamenta de las posiciones estan construidas por una mezcla componentes de tecnología GIS y componentes de tecnología AIS), por favor refierase a AIS o GIS en función del diseño específico de dicho componente. | Napomena 2: U hibridnim postrojenjima (postrojenja kod kojih polja sadrže mješavinu GIS i AIS komponenata), molim vas pogledajte definicije AIS i GIS za specifične komponente | Note 2: In hybrid switchgear (switchgear the bays of which are made from a mix of GIS and AIS technology components), please refer to AIS or GIS in dependence of specific design of the referred component. | Nota 2: La echipamentele de comutatie (echipamentele electrice) hibrid (in celulele formate din componente mixte, in tehnologie GIS si AIS), va rugam sa va referiti la AIS sau GIS in dependenta cu conceptia specifica a componentei referite. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.6 | Failure mode | 1.6 | Failure mode | Klasifikace poruchy/zavady | Failure mode | Mode de défaillance | Merkmale des Fehlers | 故障分類 | Feiltype | Tryb uszkodzenia | Tipo de Fallo | Tip kvara | Failure mode | Mod de defectare | X | X | X | X | X | X
| Failure mode describes a basic function of the equipment which the equipment is not able to meet (at major failure mode) or is able to meet with certain restrictions (minor failure mode). |  | Failure mode describes a basic function of the equipment which the equipment is not able to meet (at major failure mode) or is able to meet with certain restrictions (minor failure mode). | Tato klasifikace popisuje zakladni funkce zarizeni, ktere zarizeni jiz neni schopno plnit (klasifikace poruchy) nebo je schopno plnit s urcitymi omezenimi (klasifikace zavady) | Failure mode describes a basic function of the equipment which the equipment is not able to meet (at major failure mode) or is able to meet with certain restrictions (minor failure mode). | Le mode de défaillance décrit qu'une fonction de base que l'appareillage n'est plus capable de satisfaire (mode de défaillance principal) ou on peut rencontrer certaines restrictions (mode de défaillance mineur). | Das Fehlermerkmal beschreibt eine wesentliche Funktion eines Gerätes, die im Fehlerfall nicht (beim wesentlichen Ausfall) oder nur eingeschränkt (beim geringfügigen Ausfall) erfüllt werden konnte. | 故障モードは機器の基本機能を示すものである。ただし、故障モードで示す基本機能とは、正常な状態では直面しないような機能（重故障の場合）もしくはある制約の元で機器が直面する可能性を持つ機能（軽故障の場合）を表わす。 | Feiltype angir en grunnleggende funksjon/oppgave til utstyret som utstyret ikke er i stand til å gjennomføre (alvorlig feil / "major failure") eller kan gjennomføre med visse begrensninger (mindre alvorlig feil / "minor failure"). | Tryb uszkodzenia opisuje podstawową funkcję urządzenia (aparatu), której urządzenie to nie jest w stanie spełniać (w przypadku trybu znacznego uszkodzenia) lub jest zdolne spełniać z pewnymi ograniczeniami (tryb uszkodzenia nieznacznego) | Tipo de fallo describe una funcion basica del equipo. El equipo no es capaz de funcionar (tipo de fallo mayor) o es capaz de funcionar con ciertas restricciones (tipo de fallo menor) | Tip kvara opisuje funkciju koju oprema ne može postići (veliki kvar) ili može postići uz odgovarajuća ograničenja (mali kvar). | Failure mode describes a basic function of the equipment which the equipment is not able to meet (at major failure mode) or is able to meet with certain restrictions (minor failure mode). | Modul de defectare descrie o functie a echipamentului pe care acesta nu este capabil s-o indeplineasca (la modul de defectare majora) sau este capabil s-o indeplineasca cu anumite restrictii (la modul de defectare minora). | X | X | X | X | X | X
| NOTE: Basic functions of HV equipment are usually the following: |  | NOTE: Basic functions of HV equipment are usually the following: | Poznamka : Zakladni funkce zarizeni vvn nebo zvn jsou obvykle nasledujici : | NOTE: Basic functions of HV equipment are usually the following: | NOTE : Les fonctions de base de l'appareillage HT sont habituellement les suivantes : | Anmerkung: Wesentliche Funktionen von Hochspannungsgeräten sind im allgemeinen: | 注記：高電圧機器の基本機能は、通常、以下のように示されます。 | NOTE: De grunnleggende funksjonene til høyspenningskomponenter er vanligvis de følgende: | UWAGA: Podstwowe funkcje urządzeń (aparatów) WN są zwykle następujące: | Nota: Las funciones básicas de un equipo de alta tensión son normalmente las siguientes: | Napomena: Glavna funkcija VN opreme je slijedeća: | NOTE: Basic functions of HV equipment are usually the following: | NOTA: functiile de baza ale echipamentului de IT sunt de obicei urmatoarele: | X | X | X | X | X | X
| to perform desired switching operations (at switching equipment), including not operating when not required/controlled, |  | to perform desired switching operations (at switching equipment), including not operating when not required/controlled, | provadeni pozadovane spinaci operace (u spinacu), vcetne neprovedeni operace neni-li tato pozadovana | to perform desired switching operations (at switching equipment), including not operating when not required/controlled, | Exécuter une manœuvre désirée de commutation (équipement de commutation), y compris la stabilité alors qu'une manœuvre et requise ou pas contrôlée | das Ausführen von Schaltungen (bei Schaltgeräten), einschließlich das Nichtschalten wenn nicht gewünscht/angesteuert. | （１）開閉機器において、所要の開閉操作性能を持つこと。制御指令がない場合に操作しないことも性能の一部とみなす。 | å koble (for brytere), inkludere det å ikke koble når det ikke bes om det | wykonywanie wymaganych operacji łączeniowych (aparatura łączeniowa) włącznie z brakiem działania, kiedy nie jest ono wymagane, | desarrollar operaciónes de interrupción (en equipos de interrupción), incluyendo la no operación cuando no requiera, | provedba sklopnih operacija (na sklopnim aparatima), uključujući i mirovanje kada se ne traži sklapanje, | to perform desired switching operations (at switching equipment), including not operating when not required/controlled, | sa indeplineasca functiile de comutatie cerute (la echipamentele de comutatie), incluzand sa nu lucreze cand nu se cere / nu este controlat; | X | X | X | X | X | X
| to provide HV and low voltage insulation, |  | to provide HV and low voltage insulation, | poskytovani vysokonapetove nebo nizkonapetove izolace | to provide HV and low voltage insulation, | Assurer l'isolement HT et BT | die Sicherstellung von Hoch- oder Niederspannungsisolation | （２）高電圧、低電圧絶縁性能を有する。 | å sørge for elektrisk isolasjon (både for høyspenning og for lavspenning) | zapewnienie izolacji WN i niskiego napięcia | suministrar alta tensión y baja tensión de aislamiento | osiguravanje VN i niskonaponske izolacije, | to provide HV and low voltage insulation, | sa furnizeze izolatia de IT sau JT; | X | X | X | X | X | X
| to provide and accept signals to and from connected systems (protection systems, control systems, metering systems, auxiliary and supply systems), |  | to provide and accept signals to and from connected systems (protection systems, control systems, metering systems, auxiliary and supply systems), | poskytovani/prijimani singnalut pro/od pripojenych systemu (systemy ochran, ridici systemy, merici systemy, pomocne a napajeci systemy) | to provide and accept signals to and from connected systems (protection systems, control systems, metering systems, auxiliary and supply systems), | Fournir et recevoir les signaux des systèmes associés (systèmes de protection, systèmes de commande, systèmes de mesure, auxiliaire et circuits d'alimentation), | das zur Verfügung stellen und Verarbeiten von Signalen für/von angeschlossenen Systemen (Schutzsystem, Anlagensteuerung, Meßsystem, Hilfs- und Versorgungssysteme) | （３）接続されているシステムとの送受信機能を持つこと。（システムとは、保護用システム、制御用システム、測定用システム、補器用システムや電源システムを表わす。） | å gi og motta signaler fra tilkoblede systemer (vern, kontrollanlegg, målesystemer, etc.) | dostarczanie i odbieranie sygnałów do i z przyłączonych układów (układów zabezpieczeń, układów sterowania, układów pomiarowych, układów pomocniczych i zasilania) | suministrar y aceptar señales para y de sistemas conectados (potecciones, sistemas de control, sistemas de medida, sistemas auxiliares y de abastecimiento), | osiguravanje i prihvaćanje signala priključenih sistema (sistema zaštite, kontrolnog sistema, mjernog sistema, pomoćnog i sistema napajanja), | to provide and accept signals to and from connected systems (protection systems, control systems, metering systems, auxiliary and supply systems), | sa furnizeze si sa accepte semnale la si de la sistemele conectate (sistemele de protectie, control, masura, auxiliare si de alimentare); | X | X | X | X | X | X
| to provide self-checking (monitoring functions if they are implemented). |  | to provide self-checking (monitoring functions if they are implemented). | provadeni samokontroly (monitorovaci funkce, jsou-li soucasti zarizeni) | to provide self-checking (monitoring functions if they are implemented). | Assurer l'autocontrôle des fonctions de surveillance si elles sont mises en oeuvre. | das Ausführen einer Selbstprüfung ( Monitoring Funktion sofern vorhanden) | （４）自己監視機能を持つこと。（監視装置が適用されている場合。） | å forta selvkontroll (dersom overvåkingsutstyr er montert) | zapewnienie samo-sprawdzania (funkcje monitorowania, jeżeli dany aparat jest w wyposażony w urządzenia do monitoringu) | suministrar autocomprobación (funciones de monitorización si estan implementadas) | osiguravanje samo kontrole (sistem nadgledanja ako je ugrađen). | to provide self-checking (monitoring functions if they are implemented). | sa furnizeze autocontrol (functii de monitorizare, daca acestea sunt implementate). | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.7 | Failure | 1.7 | Failure | Udalost (porucha nebo zavada) | Failure | Défaillance | Fehler | 故障 | Feil | Uszkodzenie | Fallo | Kvar | Failure | Defectare | X | X | X | X | X | X
| Lack of performance by an item of its required function or functions. |  | Lack of performance by an item of its required function or functions. | Nedostatek ve schopnosti zarizeni plnit pozadovanou funkci nebo funkce | Lack of performance by an item of its required function or functions. | Défaut de fonctionnement d'une / de fonctions requises d'un composant | Ende der Fähigkeit eines Betriebsmittels, eine geforderte Funktion zu erfüllen | 要求される機能の欠落により所用性能を満足しなくなること。 | Manglende utførelse av en eller flere funksjoner | Brak wykonywania przez dane urządzenie (aparat) jego jednej lub wielu funkcji | No cumplimiento por un elemento de su función o funciones requeridas. | Nemogućnost provedbe funkcije ili funkcija nekog elementa. | Lack of performance by an item of its required function or functions. | Pierderea aptitudinii unei entitati de a-si indeplini functia sau functiile solicitate. | X | X | X | X | X | X
| NOTE: The occurrence of a failure does not necessarily imply the presence of a defect if the stress or the stresses are beyond those specified. |  | NOTE: The occurrence of a failure does not necessarily imply the presence of a defect if the stress or the stresses are beyond those specified. | Poznamka : Vyskyt udalosti nemusi nutne znamenat pritomnost defektu zarizeni v pripade, ze namahani zarizeni bylo mimo specifikovane meze. | NOTE: The occurrence of a failure does not necessarily imply the presence of a defect if the stress or the stresses are beyond those specified. | NOTE : L'occurrence d'une défaillance n'implique pas nécessairement la présence d'un défaut, par exemple si les efforts sont au delà de ceux spécifié. | Anmerkung: Das Auftreten eines Fehlers bedingt nicht unbedingt das Vorhandensein eines Defekts sofern die Beanspruchungen oberhalb der spezifizierten Werte liegen. | 注記：機器に負荷する単独もしくは複数のストレスが仕様値を超える場合、故障は必ずしも欠陥の存在により発生するわけではない。 | NOTE: En feilhendelse innebærer ikke nødvendigvis at det finnes defekter ved utstyret dersom påkjenningene er høyere enn utstyret er spesifisert for. | UWAGA: Wystąpienie uszkodzenia nie zawsze wiąże się z występowaniem wady, jeżeli narażenie lub narażenia dla aparatu przekraczają wartości specyfikacji technicznej. | Nota: La ocurrencia de un fallo no implica necesariamente la presencia de un defecto si la solicitación o solicitaciones estan lejos de lo especificado | Napomena: Pojava kvara ne mora uključivati prisustvo defekta ako su naprezanja ispod specificiranih. | NOTE: The occurrence of a failure does not necessarily imply the presence of a defect if the stress or the stresses are beyond those specified. | NOTA: Aparitia unei defectari nu implica in mod necesar prezenta unui defect daca solicitarea sau solicitarile sunt in afara celor specificate. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.8 | Major failure | 1.8 | Major failure | Porucha | Major failure | Défaillance majeure | Wesentlicher Ausfall (Störung) | 重故障 | Alvorlig feil ("Major failure") | Znaczne uszkodzenie | Fallo mayor | Veliki kvar | Major failure | Defectare majora | X | X | X | X | X | X
| IEC 62271-1 |  | IEC 60694 | [11 empty] | X | X | X | X | X | X
| Failure of a switchgear and control gear which causes the cessation of one or more of its fundamental functions. |  | Failure of a switchgear and control gear which causes the cessation of one or more of its fundamental functions. | Porucha rozvodneho zarizeni zpusobi ztratu jedne nebo vice jeho zakladnich funkci | Failure of a switchgear and control gear which causes the cessation of one or more of its fundamental functions. | Défaillance d'appareillages qui cause l'arrêt d'une ou plusieurs fonctions fondamentales, ex.non passage du courant, manœuvre non effectuée. | Ausfall eines Schaltgerätes, der den Verlust einer oder mehrerer seiner grundlegenden Funktionen verursacht | 一つないし複数の基本機能の停止により引き起こされる開閉装置や制御装置の故障。 | En feil ved en bryter som innebærer at bryteren ikke er i stand til å gjennomføre en eller flere av sine grunnleggende funksjoner / oppgaver | Jest to uszkodzenie aparatury łączeniowej lub sterowniczej, które powoduje utratę jednej lub wielu jej podstawowych funkcji. | Fallo de la aparamenta o del mando que ocasiona la falta de una o más de sus funciones fundamentales | Kvar u postrojenju koji uzrokuje nemogućnost provedbe jedne ili više osnovnih funkcija. | Failure of a switchgear and control gear which causes the cessation of one or more of its fundamental functions. | Defectarea unui echipament de comutatie sau de control care cauzeaza incetarea uneia sau mai multora dintre functiile sale fundamentale. | X | X | X | X | X | X
| A major failure will result in an immediate change in the system operating conditions, e.g. the backup protective equipment will be required to remove the fault, or will result in mandatory removal from service within 30 minutes for unscheduled maintenance. Note: or will result in unavailability for required service. |  | A major failure will result in an immediate change in the system operating conditions, e.g. the backup protective equipment will be required to remove the fault, or will result in mandatory removal from service within 30 minutes for unscheduled maintenance. Note: or will result in unavailability for required service. | Porucha vede k okamzite zmene v podminkach provozu site, napr. systemy ochran zapusobi k vypnuti poruchy, nebo vede k povinnemu vypnuti z provozu do 30 minut za ucelem provedeni neplanovane udrzby (opravy). Poznamka: nebo vede k tomu, ze zarizeni neni k dispozici pro pozadovany provoz | A major failure will result in an immediate change in the system operating conditions, e.g. the backup protective equipment will be required to remove the fault, or will result in mandatory removal from service within 30 minutes for unscheduled maintenance. Note: or will result in unavailability for required service. | Une défaillance majeur aura comme conséquence, un changement immédiat des conditions de fonctionnement du poste et / ou du réseau, par exemple les matériels de protection de secours seront mis en oeuvre pour éliminer le défaut, avec pour conséquence un arrêt forcé possible de service de 30 minutes pour maintenance non-programmée. Note : conséquence une indisponibilité de service | Ein wesentlicher Ausfall führt zu einer unmittelbaren Änderung des Betriebszustandes des Netzes, z. B. muss der überlagerte Schutz den Fehlzustand beseitigen, oder er führt innerhalb von 30 min vorschriftsgemäß zur Außerbetriebsetzung für eine nicht vorgesehene Instandhaltung. | 重故障とは、緊急的な系統操作を引き起こすもの、例えば保護装置の動作による事故除去、あるいは３０分以内の系統からの切離し操作を要するもの、あるいは系統上使用不可能となった機器を示す。 | En alvorlig feil ("major failure") resulterer i en umiddelbar endring i systemets driftsbetingelser, f.eks. ved vern og bakenforliggende utstyr behøves for å koble fort feilen, eller resulterer i at utstyret tvinges til å tas ut av drift innen 30 minutter for ikke-planlagt vedlikehold / reparasjon. Note: eller vil føre til at utstyret ikke er tilgjengelig for å kunne settes i drift | Znaczne uszkodzenie powoduje natychmiastową zmianę warunków ruchowych systemu np. konieczność zastosowania urządzeń zastępczych, lub też powoduje konieczność wyłączenia z pracy uszkodzonego urządzenia w ciągu 30 minut, aby wykonać nieplanowany zabieg obsługi. | Un fallo mayor provocará un cambio inmediato de las condiciones de explotación de la red, p.e. el equipo de protección secundaria o de respaldo será requerido para eliminar la falta o bien dará lugar a una puesta fuera de servicio durante 30 minutos, debido a una operación de mantenimiento no planificada. Nota: o producirá una incapacidad para el servicio requerido | Veliki kvar rezultira trenutnom promjenom u radu sistema, npr. prorada zaštite | A major failure will result in an immediate change in the system operating conditions, e.g. the backup protective equipment will be required to remove the fault, or will result in mandatory removal from service within 30 minutes for unscheduled maintenance. Note: or will result in unavailability for required service. | O defectare majora conduce la o schimbare imediata a conditiilor de operare ale sistemului, de ex. echipamentul de protectie va actiona pentru indepartarea defectului, sau va rezulta o scoatere obligatorie din functiune in timp de 30 minute pentru mentenanta neplanificata. Nota: sau va rezulta o indisponibilitate a seviciului solicitat | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.9 | Minor failure | 1.9 | Minor failure | Zavada | Minor failure | Défaillance mineure | Geringfügiger Ausfall (Schaden) | 軽故障 | Mindre alvorlig feil ("minor failure") | Nieznaczne uszkodzenie | Fallo menor | Mali kvar | Minor failure | Defectare minora | X | X | X | X | X | X
| IEC 62271-1 |  | IEC 60694 | [11 empty] | X | X | X | X | X | X
| Failure of an equipment other than a major failure or any failure, even complete, of a constructional element or a sub-assembly which does not cause a major failure of the equipment. |  | Failure of an equipment other than a major failure or any failure, even complete, of a constructional element or a sub-assembly which does not cause a major failure of the equipment. | Udalost zarizeni nebo jeho konstrukcni soucasti, ktera nezpusobi poruchu celeho zarizeni. | Failure of an equipment other than a major failure or any failure, even complete, of a constructional element or a sub-assembly which does not cause a major failure of the equipment. | Défaillance d'un composant ou d'un sous ensemble ne provoquant pas une défaillance majeure de l'appareillage nécessitant une indisponibilité de service. | Jeder Ausfall eines Bauteils oder einer Baugruppe, der nicht zu einem wesentlichen Ausfall des Schaltgerätes führt | 構成部品や補器類の故障で、重故障までは至らないもの。 | Feil som ikke er en alvorlig feil ("major failure") eller feil, til og med fullstendig, av konstruksjonsdeler eller delkomponenter som ikke fører til en alvorlig feil ("major failure") av utstyret. | Uszkodzenie urządzenia (aparatu) inne niż znaczne uszkodzenie lub jakiekolwiek inne uszkodzenie nawet całego elementu konstrukcyjnego lub podzespołu, które nie powoduje powstania znacznego uszkodzenia. | Averia en un equipo que no da lugar a fallo mayor o fallo, incluso completo, de un elemento contructivo o de un subconjunto que no causa fallo mayor del mismo. | Kvar na opremi koji nije veliki kvar i koji ne dovodi do velikog kvara. | Failure of an equipment other than a major failure or any failure, even complete, of a constructional element or a sub-assembly which does not cause a major failure of the equipment. | Defectarea unui echipament, alta decat o defectare majora sau orice alta defectare, chiar completa, a unui element constructiv sau unui subansamblu, care nu cauzeaza o defectare majora a echipamentului. | X | X | X | X | X | X
| Note: Do not mix with "defect" (IEC 60694): |  | Note: Do not mix with "defect" (IEC 60694): | Poznamka : Prosim, nezamenujte s defektem (IEC 60694): | Note: Do not mix with "defect" (IEC 60694): | Note : Ne pas confondre avec un défaut au sens de la norme CEI 60694) : | Anmerkung: Bitte nicht mit Mangel verwechseln (IEC 60694) | 注記：下記の欠陥（ＩＥＣ ６０６９４）と混同せぬように注意のこと。 | Note: Må ikke forveksles med defekt ("defect") (IEC 60694): | Nie mylić z wadą (defektem) IEC 60694) | Nota: No confundir con "Defecto" (IEC 60694) | Napomena: Ne treba ga miješati s greškom (IEC 60694): | Note: Do not mix with "defect" (IEC 60694): | Nota: a nu se confunda cu defect (IEC 60694) | X | X | X | X | X | X
| Imperfection in the state of an item (or inherent weakness) which can result in one or more failures of the item itself or of another item under the specific service or environmental or maintenance conditions for a stated period of time. |  | Imperfection in the state of an item (or inherent weakness) which can result in one or more failures of the item itself or of another item under the specific service or environmental or maintenance conditions for a stated period of time. | Defekt = nedostatek ve stavu zarizeni, ktery muze vest k jedne nebo vice porucham zarizeni sameho nebo zarizeni jineho, a to za urcitych provoznich nebo udrzbovych nebo atmosferickych podminek v urcitem (stanovenem) casovem horizontu. | Imperfection in the state of an item (or inherent weakness) which can result in one or more failures of the item itself or of another item under the specific service or environmental or maintenance conditions for a stated period of time. | Imperfection d'état d'un composant (ou faiblesse inhérente) pouvant causer une/ des défaillances du composant lui-même ou d'un autre composant dans des conditions de service particulières ou environnementales ou de maintenance pendant une période indiquée. | Unvollkommenheit des Zustandes eines Betriebsmittels (oder eine dem Betriebsmittel eigene Schwäche), die innerhalb eines festgesetzten Zeitbereiches unter bestimmten Betriebs-, Umgebungs- oder Instandhaltungsbedingungen zu einem Ausfall oder mehreren Ausfällen des Betriebsmittels selbst oder eines anderen Betriebsmittels führen kann | 決まった期間において仕様範囲内での運用条件、環境条件、メンテナンス条件下での部品の故障を引き起こす状態不完全（もしくはもともとの弱点）。 | Uregelmessighet til en del (eller innebygd svakhet) som kan gi feil på delen eller andre deler under gitte driftsbetingelser eller gitte omgivelser eller et gitt vedlikehold i et gitt tidsintervall. | Wada jest to niedoskonałość stanu danego elementu (lub osłabienie), które może powodować w rezultacie jedno lub więcej uszkodzeń tego elementu lub innych elementów w określonych warunkach pracy lub środowiska lub warunach eksploatacji w określonym okresie. | Imperfección del estado de un elemento (o inherente debilidad) que puede dar lugar a uno o más fallos del propio elemento o de otro en las condiciones específicadas de servicio, ambientales o de mantenimiento, durante un tiempo determinado. | Nepravilnosti u stanju nekog elementa (ili unutrašnje slabosti) koje mogu dovesti do jednog ili više kvarova samog elementa ali i drugih elemenata pri specifičnim uvjetima pogona, okoline ili održavanja u određenom vremenskom periodu. | Imperfection in the state of an item (or inherent weakness) which can result in one or more failures of the item itself or of another item under the specific service or environmental or maintenance conditions for a stated period of time. | Imperfectiune in starea unei entitati (sau o slabiciune inerenta) care poate rezulta in una sau mai multe defectari ale acelei entitati sau ale altei entitati in conditii specifice de exploatare sau de mediu sau de mentenanta, pe o perioada determinata. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.10 | Maintenance | 1.10 | Maintenance | Udrzba | Maintenance | Maintenance | Instandhaltung | メンテナンス | Vedlikehold | Obsługa | Mantenimiento | Održavanje | Maintenance | Mentenanta | X | X | X | X | X | X
| IEC 62271-1 ; IEV 191-07-01 |  | IEC 60694 ; IEV 191-07-01 | [11 empty] | X | X | X | X | X | X
| The combination of all technical and administrative actions, including supervision actions, intended to retain an item in, or restore it to, a state in which it can perform a required function. |  | The combination of all technical and administrative actions, including supervision actions, intended to retain an item in, or restore it to, a state in which it can perform a required function. | Kombinace vsech technickych a administrativnich ukonu, vcetne dohledu, provadenych za ucelem navraceni zarizeni do stavu, v nemz zarizeni muze plnit pozadovanou funkci | The combination of all technical and administrative actions, including supervision actions, intended to retain an item in, or restore it to, a state in which it can perform a required function. | Combinaison de toutes les actions techniques et administratives y compris des actions de surveillance, pour maintenir ou restituer a un article, un état de fonctionnement lui permettant de réaliser toutes les fonction exigées. | Kombination aller technischen und administrativen Maßnahmen einschließlich Überwachungsmaßnahmen, mit denen eine Einheit im funktionsfähigen Zustand erhalten oder in ihn zurückversetzt werden soll | 要求される機能を実行できる状態の維持、もしくはその状態への復旧を行うための、監視を含む全ての組合せの技術的・管理的作業。 | Summen av alle tekniske og administrative handlinger, inkludert ledelse, med formål å opprettholde eller gjenopprette tilstanden til en del slik at den kan utføre en angitt oppgave. | Kombinacja wszystkich technicznych i administracyjnych działań obejmująca działania kontrolne, mające na celu utrzymanie danego elementu lub przywrócenie do do stanu, w którym może wykonywać wymaganą funkcję. | Combinación de todas las técnicas y acciones administrativas, incluyendo acciones de supervisión, propuestas para conservar un elemento, o recuperar, las condiciones que le permitan desarrollar la función requerida. | Kombinacija svih tehničkih i administrativnih akcija, uključujući i akcije nadzora, s ciljem da se održi ili ponovo postigne stanje u kojem se može obavljati tražena funkcija. | The combination of all technical and administrative actions, including supervision actions, intended to retain an item in, or restore it to, a state in which it can perform a required function. | Combinatia tuturor actiunilor tehnice si administrative (organizatorice), incluzand si actiuni de supraveghere, in scopul mentinerii sau restabilirii unei entitati in starea in care isi poate indeplini functia solicitata. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.11 | Scheduled maintenance | 1.11 | Scheduled maintenance | Planovana udrzba | Scheduled maintenance | Maintenance programmée | Planmäßige Instandhaltung | 計画されたメンテナンス | Planlagt vedlikehold | Obsługa planowana | Mantenimiento programado | Propisano održavanje | Scheduled maintenance | Mentenanta planificata | X | X | X | X | X | X
| IEC 62271-1 ; IEV 191-07-10 |  | IEC 60694 ; IEV 191-07-10 | [11 empty] | X | X | X | X | X | X
| The preventive maintenance carried out in accordance with an established time schedule or with established condition based rules. |  | The preventive maintenance carried out in accordance with an established time schedule or with established condition based rules. | Preventivni udrzba provadena v souladu s urcenym casovym planem nebo na zaklade urcenych pravidel hodnoceni stavu zarizeni | The preventive maintenance carried out in accordance with an established time schedule or with established condition based rules. | Maintenance préventive effectué selon un calendrier établi ou sur des conditions d'état prédéfinies à partir de règles basées sur l'expérience. | Vorsorgende Instandhaltung, die nach eingeführten Zeitabschnitten oder Zustandsregeln durchgeführt wird. | 計画されたメンテナンスは、確立された定期点検規則と状態に基づく点検規則に従って実行される。 | Forebyggende vedlikehold gjennomført i henhold til en etablert tidsplan eller med etablerte tilstandsbaserte regler. | Profilaktyczna obsługa prowadzona zgodnie z ustalonym harmonogramem lub określonymi zasadami oceny stanu technicznego | Mantenimiento preventivo realizado de acuerdo con un programa de tiempo establecido o con unas reglas basadas en el estado del equipo. | Preventivno održavanje koje se provodi u propisanim vremenskim intervalima ili u skladu s pravilima koja ovise o stanju. | The preventive maintenance carried out in accordance with an established time schedule or with established condition based rules. | Mentenanta preventiva desfasurata pe baza unui program de timp stabilit sau a unor reguli stabilite pe baza de stare. | X | X | X | X | X | X
| Time Based: |  | Time Based: | Casove zavisla udrzba | Time Based: | Basé sur le temps | Zeitabhängig: | （１）定期点検（時間管理に基づく；TBM）: | Tidsbasert (peridisk): | Okresowa obsługa: | Basado en tiempo: | Vremenski bazirano održavanje: | Time Based: | Bazata pe Timp | X | X | X | X | X | X
| Scheduled maintenance including overhaul that is performed on defined period of time or number of operations has elapsed. |  | Scheduled maintenance including overhaul that is performed on defined period of time or number of operations has elapsed. | Casove zavisla udrzba (vcetne revize) je provadena v predem urcenem casovem intervalu nebo v intervalu urcenem prekrocenim povoleneho poctu funkci | Scheduled maintenance including overhaul that is performed on defined period of time or number of operations has elapsed. | Maintenance programmée comprenant les révisions effectuées à des périodes définies ou basée sur le nombre de manœuvres effectués. | Planmäßige Instandhaltung inkl. Überholung, die nach einem definierten Zeitraum oder Anzahl von Schalthandlungen durchgeführt wird. | 定期点検は、仕様に明記された期間や運転回数が経過した時に行われるオーバーホールも含む。 | Planlagt vedlikehold, inkludert revisjoner som er gjennomført med planlagte tidsintervaller eller etter et definert antall koblinger. | Okresowa obsługa obejmująca podstawowy zabieg obsługi (przegląd), która jest wykonywana po upływie określonego czasu lub wykonaniu określonej liczby operacji łączeniowych. | Mantenimiento programado incluyendo revisiones detalladas que se realiza en intervalos de tiempo fijos o por número de operaciones. | Propisano održavanje uključujući i remont koje se provodi u definiranim vremenskim intervalima ili nakon određenog broja sklopnih operacija. | Scheduled maintenance including overhaul that is performed on defined period of time or number of operations has elapsed. | Mentenanta planificata incluzand RK, care este executata la o perioada definita de timp sau un numar de actionari scurse. | X | X | X | X | X | X
| Condition Based: |  | Condition Based: | Udrzba zavisla na provoznim stavu | Condition Based: | Basé sur les conditions: | Zustandsabhängig: | （２）機器の状態に基づく点検（CBM） | Tilstandsbasert: | Obsługa zależna od stanu technicznego: | Basado en el estado del equipo: | Održavanje prema danim uvjetima: | Condition Based: | Bazata pe Stare | X | X | X | X | X | X
| Maintenance that measures/assesses service conditions from monitoring or diagnostic data. When the condition has changed or exceeded a limit, a condition directed task is then implemented and the item is returned to an acceptable operating condition. |  | Maintenance that measures/assesses service conditions from monitoring or diagnostic data. When the condition has changed or exceeded a limit, a condition directed task is then implemented and the item is returned to an acceptable operating condition. | Udrzba zalozena na provoznim stavu zarizeni vyhodnocenem z udaju diagnostickych mereni nebo monitorovani. Jestlize se provozni podminky zmeni nebo prekroci danne meze, je provedena cilena udrzbova prace za ucelem navraceni zarizeni do plne provozuschopneho stavu | Maintenance that measures/assesses service conditions from monitoring or diagnostic data. When the condition has changed or exceeded a limit, a condition directed task is then implemented and the item is returned to an acceptable operating condition. | Maintenance qui mesure, estime les conditions de service sur la base d'une surveillance ou de données de diagnostique, Quand la condition a changé ou a dépassé une limite, une condition correction est alors mise en application et le composant est remis dans une condition de fonctionnement acceptable. | Instandhaltung, die in Abhängigkeit von Betriebsdaten aus Monitoring oder Diagnose durchgeführt wird. Wenn ein Zustandskriterium sich verändert oder überschritten wird, wird eine Verbesserungsmaßnahme zur Wiederherstellung eines akzeptablen Zustandes durchgeführt. | 監視データや開閉特性データから運用状態を測定／評価するメンテナンス。機器の状態変化や管理値超過が認められた時は、運転状態の修理作業を実施し許容できる操作状態へ修復する。 | Vedlikhold som måler/anslår driftstilstanden ut fra overvåking eller diagnostiske data. Når tilstandsmålet er endret eller har overskedet en grenseverdi, gjennomføres et tiltak med hensikt å bringe delen tilbake til en akseptabel driftstilstand. | Obsługa, która bierze pod uwagę, ocenia warunki pracy, wyniki monitoringu, pomiarów diagnostycznych. W przypadku zmiany warunków lub przekroczenia wartości dopuszczalnych wykonywany jest zabieg obsługi, którego zakres jest określany na podstawie oceny, a którego zadaniem jest przywrócenie aparatu do akcetowanego stanu funkcjonalności. | Mantenimiento que mide o chequea las condiciones de servicio mediante monitorización o datos de diagnostico. Cuando las condiciones cambian o superan un límite, se actúa sobre el problema y el elemento recupera unas condiciones aceptables de operación. | Održavanje pri čemu se mjeri/prati stanje pomoću podataka dobivenih nadgledanjem i dijagnostikom. Kada se stanje promjeni ili premaši utvrđenu granicu, primjenjuju se mjere potrebne da se element vrati u prihvatljivo pogonsko stanje. | Maintenance that measures/assesses service conditions from monitoring or diagnostic data. When the condition has changed or exceeded a limit, a condition directed task is then implemented and the item is returned to an acceptable operating condition. | Mentenanta care evalueaza/ masoara conditiile de exploatare (starea) prin monitorizare sau diagnoza. Cand starea s-a schimbat sau a depasit o limita, o actiune directionata pe stare este efectuata si entitatea este readusa la o stare de functionare acceptabila. | X | X | X | X | X | X
| Run-to-Failure: |  | Run-to-Failure: | Bez udrzby (provoz do poruchy) | Run-to-Failure: | Fonctionnement jusqu'à la défaillance: | Fehlerabhängig: | （３）事後保全（故障が発生したら修理する） | Havaristyrt ("run-to-failure"): | Zabiegi obsługi nie są wykonywane, aż do wystąpienia uszkodzenia. | Actuación después del fallo: | Izlazak na kvar: | Run-to-Failure: | La defectare: | X | X | X | X | X | X
| Item is allowed to fail and at the time of failure, appropriate corrective actions are taken to return the item to an acceptable operating condition. |  | Item is allowed to fail and at the time of failure, appropriate corrective actions are taken to return the item to an acceptable operating condition. | Je dovoleno, aby zarizeni bylo provozovano do poruchy. Po poruse je pripadne provedena oprava. | Item is allowed to fail and at the time of failure, appropriate corrective actions are taken to return the item to an acceptable operating condition. | Le composant est utiliser jusqu'a la rupture, des dispositions sont prises pour une remise en état afin d'obtenir des conditions de fonctionnement acceptable. | Das Gerät darf einen Fehler aufweisen. Erst nach dem Fehlereintritt werden Korrekturmaßnahmen ergriffen um das Gerät wieder in einen akzeptablen Zustand zu versetzen. | 故障と見込まれるアイテムがある時もしくは故障発生時に、許容される操作状態の復旧するために行われる適切な臨時点検。 | Delen tillates å feile og når dette skjer iverksettes hensiktsmessige korrektive tiltak for å bringe delen tilbake til en akseptabel driftstilstand. | Dopuszcza się uszkodzenie aparatu, a w momencie wystąpienia uszkodzenia stosowne działania naprawcze sa podejmowane, w celu przywrócenia aparatu do akceptowanego stanu funkcjonalności. | El elemento puede fallar y durante el tiempo de fallo, se toman las acciones correctivas apropiadas para devovel al elemento unas condiciones aceptables de operaciòn. | Dopušta se da dođe do kvara na elementu, a zatim se provode korektivne akcije da se vrati u prihvatljivo pogonsko stanje. | Item is allowed to fail and at the time of failure, appropriate corrective actions are taken to return the item to an acceptable operating condition. | Entitatea este lasata sa se defecteze si in momentul defectarii i se aplica actiuni corective pentru a o aduce la starea de functionare acceptabila. | X | X | X | X | X | X
| Combination (RCM): |  | Combination (RCM): | Kombinace vyse uvedenych typu udrzby (napr. RCM) | Combination (RCM): | Combinaison (RCM) : | Kombinationen (RCM): | （４）異なる方法の組合せ (RCM): | Kombinasjon av flere (f. eks. RCM): | Kombinacja różnych rodzajów obsługi (obsługa ukierunkowana na niezawodność RCM) | Combinación (p.e. RCM): | Kombinacija (RCM): | Combination (RCM): | Combinata (RCM) | X | X | X | X | X | X
| A combination of the above tasks that take into to account the affects of failure and the effectiveness of prevention. |  | A combination of the above tasks that take into to account the affects of failure and the effectiveness of prevention. | Kombinace vyse uvedenych ukolu, která bere v uvahu dusledky poruch a ucinnost jejich prevence. | A combination of the above tasks that take into to account the affects of failure and the effectiveness of prevention. | Une combinaison des tâches ci-dessus qui prend en compte les effets de la défaillance et de l'efficacité des mesures préventives. | Eine Kombination der oben genannten Instandhaltungsarten, welche die Auswirkungen der Fehler und Effektivität der Vorsorgemaßnahmen berücksichtigt. | 事故の影響や防止効果を考慮した上記の点検方法の組合せ | En kombinasjon av de overnevnte tiltakene som tar hensyn til konsekvensen av feil og muligheten til å forhindre dem. | Kombinacja wyżej wymienionych diałań, która uwzględnia skutki uszkodzenia i efektywność zapobiegania uszkodzeniu. | Un combinación de las actuaciones anteriores que tiene en cuenta las conssecuencias del fallo y la efectividad de la prevención. | Kombinacija gore spomenutih metoda koja uzima u obzir efekte kvara i efikasnost prevencije. | A combination of the above tasks that take into to account the affects of failure and the effectiveness of prevention. | O combinatie a actiunilor de mai sus, care ia in considerare consecintele defectarii si eficienta preventiei. | X | X | X | X | X | X
| Other: |  | Other: | Jina | Other: | Autre | Andere: | （５）その他： | Annen: | Inna | Otro | Drugo: | Other: | Alta | X | X | X | X | X | X
| Maintenance philosophy not described by any of the above. |  | Maintenance philosophy not described by any of the above. | Udrzbova strategie, kterou nelze popsat nicim vyse uvedenym | Maintenance philosophy not described by any of the above. | Politique de maintenance qui n'est pas décrite précédemment. | Instandhaltungsphilosophie, die nicht durch die oben genannten abgedeckt wird. | 上記の点検内容とは思想の異なるメンテナンス | Vedlikeholdsfilosofier som ikke blant dem beskrevet over. | Polityka obsługi nie opisana przez żadna z powyższych | Filosofía de mantenimiento no descrita por alguno de los anteriores tipos de mantenimiento | Filozofija održavanja koja nije opisana u gore spomenutim metodama. | Maintenance philosophy not described by any of the above. | O filozofie de mentenanta nedescrisa de nici una din cele de mai sus. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.12 | Corrective maintenance | 1.12 | Corrective maintenance | Napravna udrzba (oprava) | Corrective maintenance | Maintenance corrective | Korrigierende Instandhaltung | 臨時点検 | Reparajon / korrektivt vedlikehold | Zapobiegawczy zabieg obsługi | Mantenimiento correctivo | Korektivno održavanje | Corrective maintenance | Mentenant corectiva | X | X | X | X | X | X
| Additional work found necessary to do arising from equipment defects or failures found on other similar equipment or recommended by the manufacturer or repair of the major or minor failure or defect of the equipment itself . |  | Additional work found necessary to do arising from equipment defects or failures found on other similar equipment or recommended by the manufacturer or repair of the major or minor failure or defect of the equipment itself . | Prace navic, jejiz provedeni bylo shledano nezbytnym po odhaleni defektu nebo poruchy na jinem podobnem zarizeni nebo doporucene vyrobcem, nebo oprava po odhaleni poruchy nebo zavady nebo defektu na zarizeni samotnem. | Additional work found necessary to do arising from equipment defects or failures found on other similar equipment or recommended by the manufacturer or repair of the major or minor failure or defect of the equipment itself . | Maintenance complémentaire appliquée à un matériel pour prendre en compte une /des défaillances mineures ou majeures trouvées sur le matériel lui même ou sur un matériel similaire ou recommandée par le constructeur | Zusätzliche Arbeiten, die aufgrund von Defekten oder Fehlern an gleichartigen anderen Geräten oder nach Herstellerempfehlung oder nach der Reparatur von wesentlichen oder geringfügigen Ausfällen am gleichen Gerät für notwendig erachtet werden. | 臨時に実施される追加の点検作業。臨時点検作業は、他の同型機種の故障・欠陥の発生の場合、製造者によって推奨された場合、重故障・軽故障発生時やその機器自身の欠陥によって必要となる作業である。 | Ekstra arbeid ansett nødvendig på bakgrunn av dekfekter og feil som er funnet på annet tilsvarende utstyr eller på bakgrunn av anbefalinger fra leverandør, samt reparasjoner / feilretting . | Dodatkowa praca, której konieczność wykonania wynika z wad lub udzkodzeń stwierdzonych na innych podobnych urządzeniach (aparatach) lub zalecona przez producenta lub naprawa znacznego lub nieznacznego uszkodzenia lub usunięcia wady danego urządzenia (aparatu) | Trabajo adicional necesario que surge de equipos defectuosos o de fallos encontrados en equipos similares, por recomendación del fabricante, por reparación de fallos mayores o menores o por defectos del propio equipo. | Dodatni radovi koji su rađeni na sličnoj opremi, ili ih je propisao proizvođač, ili popravak velikog i malog kvara ili greške na samom elementu. | Additional work found necessary to do arising from equipment defects or failures found on other similar equipment or recommended by the manufacturer or repair of the major or minor failure or defect of the equipment itself . | Lucrari aditionale stabilite a fi necesare pe baza deteriorarilor si defectarilor intalnite la echipamente similare sau recomandate de fabricant, sau repararea unei defectari minore sau majore sau a unei deteriorari la echipamentul respectiv. | X | X | X | X | X | X
| Note: Observations resulting from maintenance (wherein some disassembly has been done to determine actual condition that an external inspection could not reveal) can lead to the decision to carry out other types of maintenance (including an overhaul). |  | Note: Observations resulting from maintenance (wherein some disassembly has been done to determine actual condition that an external inspection could not reveal) can lead to the decision to carry out other types of maintenance (including an overhaul). | Poznamka: Pozorovani behem udrzby mohou vest k rozhodnuti provest jiny typ udrzby, vcetne velke udrzby (revize). | Note: Observations resulting from maintenance (wherein some disassembly has been done to determine actual condition that an external inspection could not reveal) can lead to the decision to carry out other types of maintenance (including an overhaul). | Note : Observations résultant de la maintenance (ou d'un démontage fait pour déterminer l'état réel des composants, qu'une inspection externe n'aurait pu révéler) ceci peut conduire à la décision d'effectuer d'autres actions de maintenance. | Anmerkung: Erkenntnisse, die nach einer Instandhaltung (mit Demontagearbeiten zur Zustandsermittlung, die eine externe Kontrolle nicht ermöglichen würde) gewonnen werden, können zu weitergehenden Instandhaltungsmaßnahmen führen ( inkl. Überholung) | 注記: メンテナンスによる調査結果（外部診断では発見されないような実状を把握するために、部分的な分解作業が必要となる場合がある）が、その他のメンテナンス項目（オーバーホールを含む）の実施を決定する可能性もある。 | Note: Funn fra vedlikehold (der utstyr har blitt åpnet for å undersøke ting man ikke kan oppdage ved ekstern inspeksjon) kan føre til at det besluttes å gjennomføre annet type vedlikehold, (inkludert en revisjon). | Uwaga: Wnioski wynikające z zabiegów obsługi (podczas, których przeprowadzono częściowy demontaż, w celu dokonania oceny aktualnego stanu, której nie można dokonać poprzez zewnętrzną inspekcję) może prowadzić do podjęcia decyzji o przeprowadzeniu innych rodzajów zabiegów obsługi (włącznie z przeglądem) | Nota: Observaciones resultantes del mantenimiento (en el que se ha realizado un cierto desmontaje para determinar el estado actual y que una inspección externa no puede revelar) pueden llevar a tomar la de decisión de realizar otro tipo de mantenimiento (incluida una revisión detallada) | Napomena: Uočeni nedostaci za vrijeme održavanja mogu utjecati na donošenje odluke o vrsti radova održavanja uključujući i remont. | Note: Observations resulting from maintenance (wherein some disassembly has been done to determine actual condition that an external inspection could not reveal) can lead to the decision to carry out other types of maintenance (including an overhaul). | Nota: Observatiile rezultand din mentenanta (in cazul in care s-au facut demontari pentru a determina starea actuala pe care o inspectie externa nu ar fi putut-o demonstra) pot conduce la decizia de a efectua un alt tip de mentenanta (incluzand RK). | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.13 | Inspection | 1.13 | Inspection | Prohlidka | Inspection | Inspection | Inspektion | 診断 | Visuell inspeksjon: | Inspekcja | Inspección | Pregled | Inspection | Inspectie | X | X | X | X | X | X
| IEC 62271-1 |  | IEC 60694 | [11 empty] | X | X | X | X | X | X
| Periodic visual investigation of the principal features of the switchgear and control gear in service without dismantling. |  | Periodic visual investigation of the principal features of the switchgear and control gear in service without dismantling. | Pravidelna pohledova kontrola zakladnich vlastnosti rozvodneho zarizeni v provozu (bez demontaze) | Periodic visual investigation of the principal features of the switchgear and control gear in service without dismantling. | Examen visuel périodique sur les principaux sous ensemble et composants de l'appareillage en service sans démontage. | Periodische visuelle Untersuchung der Hauptmerkmale des in Betrieb befindlichen Schaltgerätes ohne dessen Demontage. | 運転状態の開閉装置や制御装置の主要構成部品の分解を伴わない定期的な外部診断。 | Periodisk visuell undersøkelse av de viktigste delene av bryteren uten at den tas ut av drift og uten at den åpnes. | Okresowe wizualne sprawdzenie podstwowych cech aparatury łączeniowej i sterowniczej będącej w pracy bez demontażu. | Control visual periódico de las características de la aparementa y del mando realizada con el equipo en servicio. | Periodička provjera osnovnih funkcija postrojenja u pogonu bez razmontiranja. | Periodic visual investigation of the principal features of the switchgear and control gear in service without dismantling. | Investigatie vizuala periodica a principalelor caracteristici ale echipamentului de comutatie si control aflat in exploatare, fara demontare. | X | X | X | X | X | X
| This investigation is generally directed toward pressures and/or levels of fluids, tightness, position of relays, pollution of insulating parts, but actions such as lubricating, cleaning, washing, etc. which can be carried out with the switchgear and control gear in service are also included. |  | This investigation is generally directed toward pressures and/or levels of fluids, tightness, position of relays, pollution of insulating parts, but actions such as lubricating, cleaning, washing, etc. which can be carried out with the switchgear and control gear in service are also included. | Tato prohlidka je obecne zamerena na kontrolu ukazatelu tlaku pripadne hladin kapalin, tesnost, polohu rele a znecisteni izolacnich casti, ale muze obsahovat i prace jako je mazani, cisteni, myti, atd., za predpokladu, ze tyto mohou byt provadeny za provozu zarizeni | This investigation is generally directed toward pressures and/or levels of fluids, tightness, position of relays, pollution of insulating parts, but actions such as lubricating, cleaning, washing, etc. which can be carried out with the switchgear and control gear in service are also included. | Cette recherche est généralement orientée vers le contrôle des pressions et/ou des niveaux de fluides, de l'étanchéité, la position des relais, la pollution des pièces isolantes, mais des actions telles que lubrifier, nettoyer, laver, etc. peuvent être effectués l'appareillage restant en service, sont aussi inclus. | Diese Untersuchung ist grundsätzlich ausgelegt auf die Überprüfung von Drücken und/oder Flüssigkeits-Füllständen, Dichtheit, Schaltstellung von Relais sowie Verschmutzung von Isolierteilen. Jedoch können auch Maßnahmen, wie z. B. Schmieren, Reinigen, Waschen usw., die bei in Betrieb befindlichem Schaltgerät erfolgen können, durchgeführt werden | この調査は、一般に、圧力、流動体の液量、気密性、リレーの位置、絶縁物の汚損度などについて実施されるが、フィールドの開閉装置や制御装置について実施される潤滑、清掃、洗浄のような作業もまた含まれる。 | Denne undersøkelsen er normal rettet mot trykk og/eller nivå på væsker og gasser, lekkasjer, releposisjoner, forurensninger på isolerende deler, men smøring, renhold som kan gjennomføres mens bryteren er i drift er også inkludert. | Sprawdzenie to dotyczy na ogół ciśnień i / lub poziomów cieczy, szczelności, pozycji przekaźników, zabrudzenia części izolacyjnych, ale także działań takich jak smarowanie, czyszczenie, mycie itp. które mogą być przeprowadzone na pracującej aparaturze łączeniowej i sterowniczej. | Este control es generalmente directo, mediante presiones y/o niveles de líquidos, estanqueidad, posición de relés, suciedad de las partes aislantes, aunque acciones como engrasar, limpiar, lavar, etc...que pueden realizarse con el interruptor en servicio estarían incluidas. | Ovo se obično odnosi na provjeru tlakova i/ili nivoa tekućina, nepropusnosti, stanja releja, zagađenja izolacijskih dijelova, ali i na radove podmazivanja, čišćenja, pranja i sl. koji se mogu obavljati i za vrijeme pogona. | This investigation is generally directed toward pressures and/or levels of fluids, tightness, position of relays, pollution of insulating parts, but actions such as lubricating, cleaning, washing, etc. which can be carried out with the switchgear and control gear in service are also included. | Aceasta investigatie este in general directionata asupra presiunii si/ sau nivelului fluidelor, etanseitatii, pozitiei releelor, poluarii partilor izolatoare, dar sunt incluse si actiuni ca lubrifiere, curatare, spalare etc care pot fi efectuate cu echipamentele in functiune. | X | X | X | X | X | X
| Note: Observations resulting from inspection can lead to the decision to carry out other types of maintenance (up to an overhaul). |  | Note: Observations resulting from inspection can lead to the decision to carry out other types of maintenance (up to an overhaul). | Poznamka: Pozorovani behem prohlidky mohou vest k rozhodnuti provest jiny typ udrzby, vcetne velke udrzby (revize). | Note: Observations resulting from inspection can lead to the decision to carry out other types of maintenance (up to an overhaul). | Note : Les observations résultant de l'inspection peuvent mener à la décision d'effectuer d'autres types de maintenance jusqu'à une révision plus complète. | Anmerkung: Die Beobachtungen, die während einer Inspektion gemacht werden, können zur Entscheidung führen, eine Überholung durchzuführen. | 注記：診断の調査結果から、その他のメンテナンス（オーバーホールまで実施される場合あり）の実施が必要となる可能性もある。 | Note: Funn fra slik annen undersøkelse kan føre til en beslutning om å gjennomføre andre typer vedlikehold (t.o.m. en revisjon). | Uwaga: Wnioski wynikające z przeprowadzonej inspekcji mogą prowadzić do decyzji o przeprowadzeniu innych rodzajów zabiegów obsługi (z przeglądem włącznie). | Nota: Observaciones resultantes de la inspección pueden llevar a tomar la decisión de realizar otro tipo de mantenimiento (incluida una revisión detallada) | Napomena: Uočeni nedostaci za vrijeme pregleda mogu utjecati na donošenje odluke o vrsti radova održavanja, uključujući i remont. | Note: Observations resulting from inspection can lead to the decision to carry out other types of maintenance (up to an overhaul). | Nota: Observatiile rezultate din inspectie pot conduce la decizia de a efectua alte tipuri de mentenanta (pana la o RK) | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.14 | Diagnostic | 1.14 | Diagnostic | Diagnostika (diagnosticke mereni) | Diagnostic | Diagnostique | Diagnoseprüfungen | 開閉特性試験、開閉操作試験（初回点検を含む） | Diagnostisk test | Diagnostyka | Medidas | Dijagnostika | Diagnostic | Diagnosticare | X | X | X | X | X | X
| IEC 62271-1 |  | IEC 60694 | [11 empty] | X | X | X | X | X | X
| Investigative tests of the characteristic parameters of switchgear and control gear to verify that it performs its functions, by measuring one or more of these parameters. |  | Investigative tests of the characteristic parameters of switchgear and control gear to verify that it performs its functions, by measuring one or more of these parameters. | Investigativni zkousky pomoci mereni jednoho nebo vice charakteristickych parametru zarizeni za ucelem stanoveni, ze zarizeni plni svoji funkci. | Investigative tests of the characteristic parameters of switchgear and control gear to verify that it performs its functions, by measuring one or more of these parameters. | Tests d'investigation des paramètres caractéristiques de l'appareillage qu'il réalise ses fonctions correctement, en mesurant un ou plusieurs des paramètres significatifs. | Vergleichende Prüfungen der Kenngrößen eines Schaltgerätes mit dem Ziel eines Funktionsnachweises durch Messung einer oder mehrerer dieser Kenngrößen | 開閉装置や制御装置が所要機能を満たすことを明確にするために、一つないし複数の特性パラメーターを測定する調査試験。 | Undersøkelse av sentrale parametre til bryteren og kontrollutstyret med formål å finne ut om det fungerer, ved å måle en eller flere av disse parametrene. | Pomiary charakterystycznych parametrów aparatury łączeniowej i sterowniczej mające na celu stwierdzenie, że jest ona zdolna do wykonywania prawidłowo swoich funkcje, poprzez pomiar jednego lub więcej tych parametrów. | Tests de control de los parámetros característicos de la aparamenta y del mando para comprobar que desarrollan sus funciones, mediante medida de uno o más de estos parámetros. | Ispitivanja karakterističnih parametara postrojenja kako bi se potvrdila njihova funkcija, mjerenjem jednog ili više tih parametara. | Investigative tests of the characteristic parameters of switchgear and control gear to verify that it performs its functions, by measuring one or more of these parameters. | Teste investigative ale parametrilor caracteristici ai echipamentelor pentru a verifica daca isi indeplineste functiile, prin masurarea unuia sau mai multora dintre acesti parametri. | X | X | X | X | X | X
| Note: The result from diagnostic tests can lead to the decision to carry out overhaul. |  | Note: The result from diagnostic tests can lead to the decision to carry out overhaul. | Poznamka : Vysledky diagnostickych zkousek mohou vest k rozhodnuti provest velkou udrzbu (revizi) zarizeni. | Note: The result from diagnostic tests can lead to the decision to carry out overhaul. | Note: Les résultats du diagnostique peuvent conduire à la décision de procéder à une remise en état générale. | Anmerkung: Das Ergebnis von Diagnoseprüfungen kann zur Entscheidung führen, eine Überholung durchzuführen. | 注記：開閉特性試験、開閉操作試験の観察結果から、オーバーホールの実施が必要となる可能性あり。 | Note: Resultatet fra en diagostisk test kan føre til en beslutning om å gjennomføre en revisjon. | Uwaga: Wyniki pomiarów diagnostycznych mogą prowadzić do podjęcia decyzji o przeprowadzeniu przeglądu. | Nota: El resultado de estas medidas pueden llevar a tomar la decisión de realizar una revisión detallada. | Napomena: Reultat dijagnostičkih ispitivanja može utjecati na odluku o provedbi remonta. | Note: The result from diagnostic tests can lead to the decision to carry out overhaul. | Nota: Rezultatele testelor de diagnoza pot conduce la decizia de a efectua o RK. | X | X | X | X | X | X
| Note: The measurement is performed on purpose (periodically or condition based) and can be performed ON/LINE or OFF/LINE. |  | Note: The measurement is performed on purpose (periodically or condition based) and can be performed ON/LINE or OFF/LINE. | Poznamka : Mereni je provadeno umyslne a s urcitym cilem (s urcitou casovou periodou nebo na zaklade provozniho stavu) a muze byt provadeno se zarizenim mimo provoz i se zarizenim v provozu | Note: The measurement is performed on purpose (periodically or condition based) and can be performed ON/LINE or OFF/LINE. | Note : La mesure des paramètres est effectuée en fonction des besoins, périodiquement ou suivant les conditions d'état ou du nombre de manœuvres et peut être réalisée en permanence en service ou périodiquement hors service. | Anmerkung: Die Messungen werden nach Bedarf (periodisch oder zustandsabhängig) durchgeführt und können online oder offline erfolgen. | 注記：測定は、（定期的に、もしくは状態に基づいて）意図的に実施され、ON/LINE、OFF/LINEの両方の状態で実施される。 | Note: Målingene gjennomføres planmessig (tidsstyrt eller tilstandsstyrt) og kan gjennomføres ON/LINE eller OFF/LINE. | Uwaga: Dany pomiar jest wykonywany celowo (okresowo lub w zależności od stanu technicznego) i może być wykonywany ON/LINE lub OFF/LINE. | Nota: La medida se realiza de forma programada (periodicamente o basada en el estado) y puede realizarse de forma ON/LINE o OFF/LINE. | Napomena: Mjerenje se provodi s određenom namjerom (periodički ili ovisno o stanju) pod naponom ili u beznaponskom stanju. | Note: The measurement is performed on purpose (periodically or condition based) and can be performed ON/LINE or OFF/LINE. | Nota: Masuratorile se efectueaza voit (periodic sau bazat pe stare) si pot fi efectuate on-line sau off-line. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.15 | Examination | 1.15 | Examination | Podrobna vnitrni prohlidka | Examination | Examen visuel | Durchsicht | 細密点検（分解点検） | Annen undersøkelse: | Sprawdzenie | Revisión | Istraživanje | Examination | Examinare | X | X | X | X | X | X
| IEC 62271-1 |  | IEC 60694 | [11 empty] | X | X | X | X | X | X
| Inspection with the addition of partial dismantling, as required, supplemented by means such as measurements and non-destructive tests in order to reliably evaluate the condition of the switchgear and control gear. |  | Inspection with the addition of partial dismantling, as required, supplemented by means such as measurements and non-destructive tests in order to reliably evaluate the condition of the switchgear and control gear. | Prohlidka vyzadujici castecnou demontaz zarizeni, doprovazena, dle pozadavku, aktivitami jako jsou mereni a nedestruktivni zkousky za ucelem spolehliveho ohodnoceni provozniho stavu rozvodneho zarizeni | Inspection with the addition of partial dismantling, as required, supplemented by means such as measurements and non-destructive tests in order to reliably evaluate the condition of the switchgear and control gear. | Une inspection avec un démontage partiel peut être nécessaire, éventuellement complété par des mesures et des essais non destructifs afin d'évaluer très exactement l'état de l'appareillage. | Inspektion mit erforderlichenfalls zusätzlicher, teilweiser Demontage und ergänzt durch Maßnahmen wie z. B. Messungen oder zerstörungsfreie Prüfungen mit dem Zweck, den Zustand des Schaltgerätes zuverlässig zu bestimmen | 部分的な分解を伴う点検作業。細密点検では、要求によって、開閉装置や制御装置の状態の信頼性評価のために測定や非破壊検査のような手法によって追加試験が実施される。 | Inspeksjon og delvis åpning, i tillegg til målinger og ikke-destruktive tester med hensikt å pålitelig vurdere tilstanden til bryteren. | Inspekcja z dodatkowym częściowym demontażem, jeżeli jest on konieczny, uzupełniona pomiarami i nieniszczącymi próbami w celu dokonania wiarygodnej oceny stanu technicznego aparatury łączeniowej i sterowniczej. | Inspección con desmontaje parcial, según se requiera, complementado con medidas y ensayos no destructivos para evaluar fielmente el estado de la aparamenta y del mando. | Pregled uz djelomično razmontiranje, u slučaju potrebe, i uz dodatak mjerenja i ne-destruktivnih ispitivanja kako bi se pouzdano odredilo stanje postrojenja. | Inspection with the addition of partial dismantling, as required, supplemented by means such as measurements and non-destructive tests in order to reliably evaluate the condition of the switchgear and control gear. | Inspectie, in plus cu demontare partiala, daca este necesar, suplimentata cu masuratori si teste nedistructive in scopul unei evaluari fiabile a echipamentului de comutatie si control. | X | X | X | X | X | X
| Note: Observations resulting from examination can lead to the decision to carry out other types of maintenance (up to an overhaul). |  | Note: Observations resulting from examination can lead to the decision to carry out other types of maintenance (up to an overhaul). | Poznamka: Pozorovani behem podrobne vnitrni prohlidky mohou vest k rozhodnuti provest jiny typ udrzby, vcetne velke udrzby (revize). | Note: Observations resulting from examination can lead to the decision to carry out other types of maintenance (up to an overhaul). | Note : Les observations résultant de l'examen peuvent conduire à la décision de devoir effectuer d'autres maintenances pouvant aller jusqu'à la remise en état générale. | Anmerkung: Untersuchungen, die aus einer Durchsicht herrühren, können zur Entscheidung über die Durchführung anderer Instandhaltungsmaßnahmen führen (bis zur Überholung). | 注記：細密点検の調査結果から、その他のメンテナンス（オーバーホールまで実施される場合あり）の実施が必要となる可能性もある。 | Note: Funn fra en visuell inspeksjon kan føre til en beslutning om å gjennomføre andre typer vedlikehold (t.o.m. en revisjon). | Uwaga: Wyniki sprawdzenia mogą prowadzić do podjęcia decyzji o przeprowadzeniu innych rodzajów zabiegów obsługi (z przeglądem włącznie). | Nota: Observaciones resultantes de la revisión pueden llevar a tomar la decisión de realizar otro tipo de mantenimiento (incluida una revisión detallada) | Napomena: Rezultat istraživanja može dovesti do odluke o provođenju drugih vrsta održavanja (uključujući i remont). | Note: Observations resulting from examination can lead to the decision to carry out other types of maintenance (up to an overhaul). | Nota: Observatiile rezultate din examinare pot conduce la decizii de a efectua alte tipuri de mentenanta (pana la o RK). | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.16 | Overhaul (Major Maintenance) | 1.16 | Overhaul (Major Maintenance) | Velka udrzba (revize) | Overhaul (Major Maintenance) | Maintenance majeure, remise en état générale. | Überholung | オーバーホール (Major Maintenance) | Revisjon / overhaling | Przegląd (podstawowy zabieg obsługi) | Revisión detallada (Mantenimiento mayor o principal) | Remont (generalni remont) | Overhaul (Major Maintenance) | RK (Mentenanta Majora) | X | X | X | X | X | X
| IEC 62271-1 |  | IEC 60694 | [11 empty] | X | X | X | X | X | X
| Work done with the objective of repairing or replacing parts which are found to be out of tolerance by inspection, test, examination, or as required by the manufacturer's maintenance manual, in order to restore the component and/or the switchgear to an acceptable condition. |  | Work done with the objective of repairing or replacing parts which are found to be out of tolerance by inspection, test, examination, or as required by the manufacturer's maintenance manual, in order to restore the component and/or the switchgear to an acceptable condition. | Prace provadene s cilem opravy nebo vymeny casti, jejichz parametry byly behem prohlidky, diagnostickych zkousek nebo podrobne vnitrni prohlidky shledany mimo tolerance nebo casti, ktere maji byt podle navodu vyrobce vymeneny. Cilem prace je obnova plne provozuschopnosti zarizeni. | Work done with the objective of repairing or replacing parts which are found to be out of tolerance by inspection, test, examination, or as required by the manufacturer's maintenance manual, in order to restore the component and/or the switchgear to an acceptable condition. | Maintenance réalisée avec l'objectif de réparer ou de remplacer les pièces qui s'avèrent hors tolérance par inspection, essai, examen, ou selon les exigences du manuel de l'entretien du constructeur, afin de remettre l'ensemble de l'appareillage en conformité avec les besoins. | Reparaturarbeiten oder Arbeiten zum Austausch oder der Aufarbeitung von Teilen, die bei Inspektionen, Prüfungen oder Durchsichten außerhalb der Toleranz lagen oder nach dem Instandhaltungshandbuch des Herstellers auszutauschen sind, um die Komponente und/oder das Schaltgerät wieder in ordnungsgemäßen Zustand zu versetzen | 開閉装置やその構成部品を許容できる性能まで復旧するために、診断、試験、細密点検により管理値外れが発見された部品の修復や交換の目的、または、製造者の取扱い説明書の手順に従って行われる作業。 | Arbeid som utføres for å reparere eller erstatte deler som viser seg å være uakseptabelt dårlige, eller som i henhold til manualen skal erstattes, i den hensikt å gjeninnsette komponenten til en akseptabel tilstand. | Są to prace mające na celu naprawę lub wymianę części, które na podstawie oceny w wyniku inspekcji, pomiarów, sprawdzenia zostają uznane jako nie spełniające dopuszczalnych tolerancji lub których wymiana w czasie przeglądu jest wymagana przez fabryczną instrukcję obsługi, w celu przywrócenia danemu elementowi i / lub aparatowi akceptowanego stanu technicznego. | Trabajo realizado con el objetivo de reparar o reemplazar partes que se han encontrado fuera de tolerancia en una inspección, ensayo o revisión o como requerimiento del manual de mantenimiento del fabricante, con el objetivo de devolver al componente y/o a la aparamenta a unas condiciones aceptables. | Radovi koji se provode u svrhu popravka ili zamjene dijelova za koje je nađeno na osnovu pregleda, ispitivanja ili proizvođačevih uputa, da su izvan propisanih tolerancija, a u cilju da se komponenta i/ili postrojenje dovedu u zadovoljavajuće pogonsko stanje. | Work done with the objective of repairing or replacing parts which are found to be out of tolerance by inspection, test, examination, or as required by the manufacturer's maintenance manual, in order to restore the component and/or the switchgear to an acceptable condition. | Lucrare efectuata cu scopul de a repara sau inlocui parti componente gasite in afara marjelor admisibile la inspectie, teste, examinari, sau cerute de manualul de mentenanta al fabricantului, pentru a restabili starea acceptabila a componentei sau/si a echipamentului. | X | X | X | X | X | X
| Note : For the purpose of this questionnaire the major maintenance = Overhaul. |  | Note : For the purpose of this questionnaire the major maintenance = Overhaul. | Poznamka : Pro ucely tohoto dotazniku je velka udrzba rovna revizi. | Note : For the purpose of this questionnaire the major maintenance = Overhaul. | Note : Pour les besoins de ce questionnaire Maintenance majeure = Remise en état générale. | Anmerkung: Für diese Umfrage setzen Sie bitte Hauptinstandhaltung (major maintenance) = Überholung | 注記：本調査内のＭajor maintenanceは、オーバーホール（Overhaul）と同義とします。 | Note : I dette skjemaet er revisjon det samme som overhaling. | Uwaga: Dla celów niniejszej ankiety należy przyjmować, że podstawowy zabieg obsługi = przeglądowi. | Nota: Para el objetivo de este cuestionario el mantenimiento mayor o principal = Revisión detallada. | Napomena: Za potrebe ove ankete velika revizija=remont | Note : For the purpose of this questionnaire the major maintenance = Overhaul. | Nota: Pentru scopul acestui chestionar mentenanta majora = RK | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
1.17 | Monitoring | 1.17 | Monitoring | Monitorovani | Monitoring | Surveillance | Kontinuierliche Überwachung (Monitoring) | モニタリング（監視） | Kontinuerlig overvåking | Monitoring | Monitorización | Nadgledanje | Monitoring | Monitorizare | X | X | X | X | X | X
| Continuous service procedure on HV equipment in service which uses a permanently installed device intended to observe automatically the state of an item, i.e. intended to measure and evaluate of one or more characteristic parameter of switchgear and control gear to verify that it performs its functions. |  | Continuous service procedure on HV equipment in service which uses a permanently installed device intended to observe automatically the state of an item, i.e. intended to measure and evaluate of one or more characteristic parameter of switchgear and control gear to verify that it performs its functions. | Trvaly provozni proces provadeny na zarizeni vvn nebo zvn v provozu, ktery vyuziva trvale nainstalovana cidla, jejichz ukolem je trvale automaticky sledovat hodnotu urciteho stavu, tj. jejichz ukolem je merit a vyhodnocovat jeden nebo vice charakteristickych parametru, ktere urcuji, ze zarizeni plni svoji funkce. | Continuous service procedure on HV equipment in service which uses a permanently installed device intended to observe automatically the state of an item, i.e. intended to measure and evaluate of one or more characteristic parameter of switchgear and control gear to verify that it performs its functions. | La surveillance en continu d'un appareillage HT en service, signifie qu'un dispositif installé de manière permanente permet d'observer automatiquement l'état d'un sous-ensemble, c.-à-d. prévu pour mesurer et évaluer un ou plusieurs paramètres caractéristiques pour vérifier que l'appareillage fonctionne correctement. | Kontinuierliche, automatisch ausgeführte Prozedur an Hochspannungsgeräten zur Beobachtung des Zustands einer Einheit. Zur Sicherstellung einer einwandfreien Funktion werden hierbei permanent am Gerät installierte Sensoren genutzt um eine oder mehrere charakteristische Parameter des Gerätes oder seiner Überwachungseinrichtung zu messen und auszuwerten. | フィールド上の高電圧機器の状態を自動的に診断するために設置された装置を用いて行われる継続的な点検手法。すなわち、開閉装置や制御装置がその機能を実行する能力を持つことを明確にするために、一つ、もしくは複数の特性パラメーターの測定、評価を実施する。 | Kontinuerlig overvåking under drift av høyspenningsutstyr basert på bruk av permanent installert utstyr som automatisk følger med tilstanden til delen, dvs. måler og evaluerer en eller flere karakteristiske parametre i den hensikt å verifisere at delen fungerer som den skal. | Ciągła procedura obsługi pracujących urządzeń (aparatury), która wykorzystuje zainstalowane na stałe urządzenia, przeznaczone do automatycznej kontroli (obserwacji) stanu technicznego danego elementu, tj. przeznaczonej do pomiaru i oceny jednego lub więcej charakterystycznych parametrów aparatury łączeniowej i sterowniczej w celu sprawdzenia, czy spełnia ona swoje funkcje. | Procedimiento o sistema de control continuo en aparamenta de alta tensión en servicio, en el cual mediante un equipo instalado permanentemente se intenta observar el estado de una cuestión, p.e. se intenta medir y evaluar uno o más parámetros característicos del interruptor y del mando para comprobar que desarrolla sus funciones | Kontinuirane servisne procedure na VN opremi tijekom pogona koje koriste trajno instalirane uređaje za automatsko motrenje stanja nekog elementa. | Continuous service procedure on HV equipment in service which uses a permanently installed device intended to observe automatically the state of an item, i.e. intended to measure and evaluate of one or more characteristic parameter of switchgear and control gear to verify that it performs its functions. | Procedura in exploatare continua a echipamentelor de IT aflate in exploatare care utilizeaza dispozitive instalate permanent pentru a observa in mod automat starea unei entitati, de ex prin masurarea si evaluarea unuia sau mai multor parametri caracteristici ai echipamentului de comutatie si control pentru a verifica daca acesta isi indeplineste functiile. | X | X | X | X | X | X
| Note: Do not mix with "diagnostic measurements" (see definition 1.14) |  | Note: Do not mix with "diagnostic measurements" (see definition 1.14) | Poznamka: Nezamenujte s diagnostickymi zkouskami (viz definice 1.14) | Note: Do not mix with "diagnostic measurements" (see definition 1.14) | Note : Ne pas mélanger avec des mesures pour un diagnostique (voir la définition 1.14) | Anmerkung: Bitte nicht mit Diagnoseprüfungen verwechseln (siehe Definition 1.14) | 注記：開閉特性試験、開閉操作試験と定義を混同しないように注意のこと。(定義 1.14項を参照のこと。) | Note: Må ikke forveksles med "diagnostisk måling" (se definisjon 1.14) | Uwaga: Nie mylić z pomiarami diagnostycznymi (patrz definicja 1.14) | Nota: No confundir con medidas de diagnosticos (ver definición 1.14) | Napomena: Nemojte pomiješati s Dijagnostičkim ispitivanjima (vidi definiciju 1.14) | Note: Do not mix with "diagnostic measurements" (see definition 1.14) | Nota: a nu se confunda cu "masuratori de diagnoza" (vezi definitia 1.14) | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
2.1 | Circuit Breaker | 2.1 | Circuit Breaker | Vypinac | Circuit Breaker | Disjoncteur | Leistungsschalter | 遮断器 | Effektbryter | Wyłącznik | Interruptor automatico | Prekidač | Circuit Breaker | Intreruptor | X
| IEC 60050; IEV 441-14-20 |  | IEC 60050; IEV 441-14-20 | [11 empty] | X
| A mechanical switching device, capable of making, carrying and breaking currents under normal circuit conditions and also making, carrying for a specified time and breaking currents under specified abnormal circuit conditions such as those of short circuit. |  | A mechanical switching device, capable of making, carrying and breaking currents under normal circuit conditions and also making, carrying for a specified time and breaking currents under specified abnormal circuit conditions such as those of short circuit. | Mechanicke spinaci zarizeni schopne zapinat, prenaset a vypinat proudy za normalnich provoznich podminek site, a tez schopne zapinat, po urcitou dobu prenaset a vypinat proudy za specifikovanych nenormalnich provoznich podminek site jako jsou zkraty | A mechanical switching device, capable of making, carrying and breaking currents under normal circuit conditions and also making, carrying for a specified time and breaking currents under specified abnormal circuit conditions such as those of short circuit. | Un appareil de coupure de courant, capables d'établir le courant, le faire transiter, le couper dans des conditions normales de service, mais aussi d'établir, faire transiter pour une durée déterminer et enfin couper le courant de court-circuit dans des conditions spécifié. | Ein mechanisches Schaltgerät, dass in der Lage ist bei normalen Betriebsbedingungen Ströme einzuschalten, zu führen und auszuschalten. Auch bei spezifizierten abnormalen Betriebsbedingungen wie Kurzschlüssen können Ströme eingeschaltet, für eine definierte Zeit geführt und ausgeschaltet werden. | 機械的に開閉動作を行なう機器であり、通常運転時の定格電流の通電、投入、遮断が可能であるとともに仕様範囲内の故障電流の短時間通電、投入、遮断を行なう能力を有する機器である。 | En mekanisk bryteinnretning som er i stand til å koble inn, føre og bryter strømmer under normale driftsbetingelser, og også å koble inn, føre for en spesifisert tid, og bryte strømmer under unormale driftsbetingelser som eksempelsvis under en kortslutning. | Jest to mechaniczne urządzenie łączeniowe, zdolne do załączania, przewodzenia i wyłączania prądów w normalnych warunkach pracy a także załaczania, przewodzenia przez określony czas i wyłączania prądów w określonych zakłóceniowych takich jak zwarcie. | Un dispositivo mecánico de interrupción, capaz de establecer, conducir y cortar corrientes en condiciones normales y también capaz de establecer, conducir durante un determinado tiempo y cortar corrientes bajo determinadas condiciones anormales de la red, tales como cortocircuitos. | Mehanički sklopni aparat, sposoban da uklapa, vodi i prekida struju u normalnim pogonskim uvjetima i također uklapa, vodi određeno vrijeme i prekida struju u nenormalnim pogonskim uvjetima kao što je npr. kratki spoj. | A mechanical switching device, capable of making, carrying and breaking currents under normal circuit conditions and also making, carrying for a specified time and breaking currents under specified abnormal circuit conditions such as those of short circuit. | Echipament de comutatie mecanic, capabil de a stabili, conduce sau intrerupe curenti in conditii normale (la curenti nominali) sau de asemenea, de a stabili, conduce sau intrerupe curenti in conditii specificate anormale, de ex. de scurtcircuit. | X
X
2.2 | Live Tank Circuit Breaker | 2.2 | Live Tank Circuit Breaker | Vypinac s porcelanem komory pod napetim (live tank) | Live Tank Circuit Breaker | Disjoncteur sous enveloppe porcelaine ou composite isolé dans l'air | Live Tank Leistungsschalter | 碍子形遮断器 | "Live tank" effektbryter | Wyłącznik "Live tank" | Interruptor de tanque vivo (convencional) | Live Tank prekidač (slobodnostojeći) | Live Tank Circuit Breaker | Intreruptor "Live Tank" | X
| IEC 60050 ; IEV 441-14-26 |  | IEC 60050 ; IEV 441-14-26 | [11 empty] | X
| A circuit-breaker with interrupters in a tank insulated from earth. |  | A circuit-breaker with interrupters in a tank insulated from earth. | Vypinac s vypinacimi komorami umistenymi v pouzdre izolovanem od zeme | A circuit-breaker with interrupters in a tank insulated from earth. | Disjoncteur avec une enveloppe de chambre de coupure isolé de la terre | Leistungsschalter mit Unterbrechereinheiten in einem vom Erdpotential isolierten Behälter. | 消弧室極間部もしくはその容器が気中絶縁となる遮断器。 | Effektbryter med brytestedene inne i et kammer som er isolert fra jord. | Wyłącznik, którego komory gaszące są odizolowane od ziemi | Un interruptor con las cámaras en una envolvente aislada de tierra | Prekidač s prekidnom komorom u kučištu (obično od porculana) izoliranom od zemlje | A circuit-breaker with interrupters in a tank insulated from earth. | Un intreruptor intr-un container izolat la pamant. | X
2.3 | Dead Tank Circuit Breaker | 2.3 | Dead Tank Circuit Breaker | Vypinac s komorou v uzemnenem pouzdre (dead tank) | Dead Tank Circuit Breaker | Disjoncteur Dead Tank | Dead Tank Leistungsschalter (Kesselschalter) | 単体ＧＣＢ | "Dead tank" effektbryter | Wyłącznik "Dead tank" | Interruptor de tanque muerto | Dead Tank prekidač (u metalnom kučištu) | Dead Tank Circuit Breaker | Intreruptor "Dead Tank" | X
| IEC 60050 ; IEV 441-14-25 |  | IEC 60050 ; IEV 441-14-25 | [11 empty] | X
| A circuit breaker with interrupters in an earthed metal tank. |  | A circuit breaker with interrupters in an earthed metal tank. | Vypinac s vypinacimi komorami umistenymi v kovovem uzemenem pouzdre | A circuit breaker with interrupters in an earthed metal tank. | Disjoncteur avec une enveloppe de chambre de coupure métallique relié à la terre. | Leistungsschalter mit Unterbrechereinheiten in einem geerdeten Behälter. | 接地された金属容器に消弧室極間部が収納された遮断器。 | Effektbryter med brytestedene inne i et jordet kammer. | Wyłącznik, którego komory gaszące są umieszczone w uziemionej obudowie | Un interruptor con las cámaras en una envolvente metalica conectada a tierra. | Prekidač s prekidnom komorom u uzemljenom metalnom kučištu | A circuit breaker with interrupters in an earthed metal tank. | Un intreruptor intr-un container metalic pus la pamant. | X
X
2.4 | Circuit Switcher | 2.4 | Circuit Switcher | Spinac obvodu (stykac) | Circuit Switcher | Circuit Switcher | Lastschalter | Circuit Switcher | "Circuit switcher" (Finnes ikke i Norge) | Circuit Switcher (łącznik obwodu) | Interruptor | Circuit Switcher | Circuit Switcher | Contactor | X
| IEEE C37.100 |  | IEEE C37.100 | [11 empty] | X
| A mechanical switching device with an integral interrupter, suitable for making, carrying, and interrupting currents under normal circuit conditions. |  | A mechanical switching device with an integral interrupter, suitable for making, carrying, and interrupting currents under normal circuit conditions. | Mechanicke spinaci zarizeni schopne zapinat, prenaset a vypinat proudy za normalnich provoznich podminek site a schopne po urcity cas prenaset proudy za specifikovanych nenormalnich provoznich podminek site jako jsou zkraty | A mechanical switching device with an integral interrupter, suitable for making, carrying, and interrupting currents under normal circuit conditions. | Dispositif mécanique de commutation avec une chambre de coupure appropriée, pour établir, transiter et couper le courant nominale dans des conditions normales. | Ein mechanisches Schaltgerät mit einer integrierten Schaltkammer, dass in der Lage ist bei normalen Betriebsbedingungen Ströme einzuschalten, zu führen und auszuschalten. | 機械的に開閉動作を行なう機器であり、通常運転時の定格電流の投入、通電、遮断能力を持つ消弧室を有する。 |  | Jest to mechaniczne urządzenie łączeniowe, zdolne do załączania, przewodzenia i wyłączania prądów w normalnych warunkach pracy. | Un dispositivo mecanico de interrupción con un dispositivo de interrupción integrado, capaz de establecer, conducir y cortar corrientes bajo condiciones normales de la red. | Mehanički sklopni aparat sa integriranom prekidnom komorom, sposoban za uklapanje, vođenje i prekidanje struje u normalnim pogonskim uvjetima. | A mechanical switching device with an integral interrupter, suitable for making, carrying, and interrupting currents under normal circuit conditions. | Echipament de comutatie mecanic cu un intreruptor integral, potrivit pentru a stabili, conduce si intrerupe curenti in conditii normale. | X
| It is also suitable for interrupting specified short-circuit current that may be less than its close and latch, momentary, and short-time current ratings. |  | It is also suitable for interrupting specified short-circuit current that may be less than its close and latch, momentary, and short-time current ratings. | Je rovnez schopen vypinat zkratovy proud urcite velikosti. | It is also suitable for interrupting specified short-circuit current that may be less than its close and latch, momentary, and short-time current ratings. | Il est également possible d'interrompre un courant de court-circuit spécifié qui est inférieur au courant de court circuit nominale du poste. | Es ist ebenfalls geeignet spezifizierte Kurzschlussströme zu unterbrechen, die möglicherweise unterhalb der Nennwerte von Einschaltstrom, Kurzzeitstrom, Stoßstrom liegen. | また、仕様範囲内の故障電流の短時間通電、投入、遮断を行なう能力を有する機器である。 |  | Łącznik taki jest także zdolny do wyłączania określonego prądu zwarciowego, który może być mniejszy niż jego wytrzymywany, krótkotrwały prąd zwarciowy, w stanie zamkniętym i zablokowanym. | Es también capaz de interrumpir corrientes de cortocircuito especificadas que pueden ser menores en que las de cierre y bloqueo, momentaneamente, y corrientes durante corto tiempo. | Također može biti sposoban za prekidanje specifičnih struja kratkog spoja koje mogu biti manje od njegove nazivne kratkospojne struje. | It is also suitable for interrupting specified short-circuit current that may be less than its close and latch, momentary, and short-time current ratings. | Este de asemenea capabil sa intrerupa curenti specifici de scurtcircuit care pot fi mai mici decat cei de inchidere, momentani si nominali de durata scurta. | X
| Note: Re-closing operation is not necessary for the circuit switcher. |  | Note: Re-closing operation is not necessary for the circuit switcher. | Poznamka: Neprovadi automaticke opetne zapnuti. | Note: Re-closing operation is not necessary for the circuit switcher. | Note : la manœuvre de refermeture n'est pas imposée pour le Circuit Switcher. | Anmerkung: Die Fähigkeit zur Wiedereinschaltung ist für Lastschalter nicht notwendig | 注記：Circuit switcherは、高速再閉路の仕様は必要としない。 |  | Uwaga: Operacja powtórnego załączania nie jest konieczna dla tego rodzaju łączników | Nota: Reenganche no es necesario en los interruptores | Napomena: Automatski ponovni uklop nije potreban. | Note: Re-closing operation is not necessary for the circuit switcher. | Nota: Operatia de reinchidere nu este necesara pentru contactor. | X
X
2.5 | Switch (Load Break Switch) | 2.5 | Switch (Load Break Switch) | Odpinac | Switch (Load Break Switch) | Interrupteur | Lastschalter | 負荷開閉器 (load break switch) | Lastbryter (finnes ikke i Norge for de aktuelle spenningsnivåer) | Łącznik (łącznik obciążenia - rozłącznik) | Seccionador de corte en carga | Sklopka (teretna sklopka) | Switch (Load Break Switch) | Separator de sarcina | X
| IEC 60050 ; IEV 441-14-10 |  | IEC 60050 ; IEV 441-14-10 | [11 empty] | X
| A mechanical switching device capable of making, carrying and breaking currents under normal circuit conditions which may include specified operating overload conditions and also carrying for a specified time currents under specified abnormal circuit conditions such as those of short circuit. |  | A mechanical switching device capable of making, carrying and breaking currents under normal circuit conditions which may include specified operating overload conditions and also carrying for a specified time currents under specified abnormal circuit conditions such as those of short circuit. | Mechanicke spinaci zarizeni schopne zapinat, prenaset a vypinat proudy za normalnich provoznich podminek site, ktere mohou zahrnovat i urcita provozni pretizeni a schopne po urcity cas prenaset proudy za specifikovanych nenormalnich provoznich podminek site jako jsou zkraty | A mechanical switching device capable of making, carrying and breaking currents under normal circuit conditions which may include specified operating overload conditions and also carrying for a specified time currents under specified abnormal circuit conditions such as those of short circuit. | Dispositif mécanique de commutation capable, d'établir, de transiter et couper le courant en situation normale de service, il peut aussi inclure des conditions de fermeture/ ouverture en condition de surcharge, mais aussi de fermer, de transiter dans un temps limité le courant de court-circuit spécifiées. | Ein mechanisches Schaltgerät, dass in der Lage ist bei normalen Betriebsbedingungen Ströme einzuschalten, zu führen und auszuschalten. Hierin können spezifizierte Überlastschaltungen als auch das Führen bestimmter zeitlich begrenzter Ströme unter besonderen Betriebsbedingungen (z.B. Kurzschluss) beinhaltet sein. | 通常運転時の定格電流の投入、通電、遮断能力を持つ機械的開閉装置であり、仕様規定内の負荷電流の開閉能力および短絡条件での仕様規定内の短時間電流通電能力を有する。 |  | Jest to mechaniczne urządzenie łączeniowe, zdolne do załączania, przewodzenia i wyłączania prądów w normalnych warunkach pracy, które mogą obejmować określone warunki przeciążenia, a także określone warunki zakłóceniowe, takie jakie mogą występować przy zwarciu. | Un dispositivo mecánico de interrupción capaz de establecer, conducir y cortar corrientes bajo condiciones normales del circuito, las cuales pueden incluir condiciones de sobrecarga especificadas y también, conducir, durante un determinado tiempo, corrientes bajo condiciones anormales de la red, tales como cortocircuitos. | Mehanički sklopni aparat sposoban za uklapanje, vođenje i prekidanje struje u normalnim pogonskim uvjetima uključujući i specifična preopterećenja, kao i kratkotrajno vođenje struje u nenormalnim pogonskim uvjetima kao što je npr. kratki spoj. | A mechanical switching device capable of making, carrying and breaking currents under normal circuit conditions which may include specified operating overload conditions and also carrying for a specified time currents under specified abnormal circuit conditions such as those of short circuit. | Echipament de comutatie mecanic, capabil de a stabili, conduce si intrerupe curenti in conditii normale care pot include conditii specificate de suprasarcina de exploatare si de asemenea pentru un timp limitat conducerea de curenti in conditii sub cele anormale specificate, ca de ex acelea de scurtcircuit. | X
| Note: A switch may be capable of making but not breaking short-circuit currents or only to switch the load current of specified characteristics such as shunt capacitor, shunt reactor or resistive currents. |  | Note: A switch may be capable of making but not breaking short-circuit currents or only to switch the load current of specified characteristics such as shunt capacitor, shunt reactor or resistive currents. | Poznamka : Odpinac muze byt schopen zapinat, avsak nikoliv vypinat, zkratove proudy, nebo muze byt schopen pouze spinat zatezove proudy specifickych charakteristik jako proudy pri spinani tlumivek, kondenzatoru nebo odporove proudy. | Note: A switch may be capable of making but not breaking short-circuit currents or only to switch the load current of specified characteristics such as shunt capacitor, shunt reactor or resistive currents. | Note : L'interrupteur permet une fermeture sur court circuit mais ne permet pas la coupure de courant des courants de court-circuit lors d'un défaut, il peut dans certains cas être utilisé pour la manœuvre des condensateurs shunt, réactance shunt. | Anmerkung: Ein Lastschalter ist möglicherweise in der Lage Kurzschlussströme einzuschalten aber nicht auszuschalten. Oder er ist in der Lage die Lastströme bestimmter Betriebsmittel wie z. B. Drosselspulen, Kapazitäten oder Widerständen zu schalten. | 注記：負荷開閉器は、短絡電流の投入能力は持つが、遮断能力は持たない。また、負荷開閉器は、コンデンサバンク、シャントリアクトや抵抗により発生する仕様規定内の負荷電流開閉能力を有する。 |  | Uwaga: Rozłącznik może być zdolny do załaczania, ale nie wyłączania prądów zwarciowych lub tylko do łaczenia prądów obciążenia, takich jak kondensatory i dławiki równoległe lub prądów rezystorów. | Nota: Un seccionador de corte en carga puede ser capaz de establecer pero no de cortar corrientes de cortocircuito o solo conmutar corrientes de carga de determinadas características tales como condensadores, reactancias o corrientes resistivas. | Napomena: Sklopka može biti sposobna da uklopi ali ne i da isklopi struju kratkog spoja, ili da sklapa struje tereta specificiranih karakteristika kao što su npr. prigušnice ili otpornici. | Note: A switch may be capable of making but not breaking short-circuit currents or only to switch the load current of specified characteristics such as shunt capacitor, shunt reactor or resistive currents. | Nota: Un separator de sarcina poate fi capabil de a stabili, dar nu de a intrerupe curenti de scurtcircuit sau numai de a comuta curenti de sarcina cu caracteristici specificate cum ar fi condensatoare, reactante sau curenti rezistivi. | X
| Note: A switch often is also called a “load break switch”. |  | Note: A switch often is also called a “load break switch”. | Poznamka : Tento spinac je často nazyvan "vypinac zateze". | Note: A switch often is also called a “load break switch”. | Note : L'interrupteur est aussi souvent appelé "Sectionneur de coupure en charge". |  | 注記: 開閉器は、 “負荷開閉器（load break switch）”とも呼ばれる。（日本は、負荷開閉器のみ。） |  | Uwaga: Łącznik jest także często nazywany "rozłącznikiem". |  | Napomena: Sklopka se često naziva i "teretna sklopka" | Note: A switch often is also called a “load break switch”. | Nota: Acest comutator se numeste "separator de sarcina" | X
X
2.6 | Does not close on command; Does not open on command | 2.6 | Does not close on command; Does not open on command | Nezapnul na povel; Nevypnul na povel | Does not close on command; Does not open on command | Ne se ferme pas sur ordre, Ne s'ouvre pas sur ordre | Schließt nicht auf Kommando; öffnet nicht auf Kommando | 閉極不能、開極不能 | Kobler ikke på kommando | Nie zamyka się po podaniu impulsu; Nie otwiera się po podaniu impulsu | No cierra a la orden; No abre a la orden | Ne uklapa na komandu; Ne isklapa na komandu | Does not close on command; Does not open on command | Nu inchide la comanda; Nu deschide la comanda | X | X
| This kind of failure refers to the electrical control and/or mechanical operation of the circuit breaker. |  | This kind of failure refers to the electrical control and/or mechanical operation of the circuit breaker. | Tento druh poruchy vypovida o elektrickem ovladani nebo o mechanicke funkci vypinace | This kind of failure refers to the electrical control and/or mechanical operation of the circuit breaker. | Ce genre de défaillance concerne soit l'ordre de commande électrique et/ou le fonctionnement mécanique du disjoncteur. | Dieser Fehlertyp bezieht sich auf die elektrische Steuerung und/oder den mechanischen Betrieb des Leistungsschalters | 遮断器の電気的な制御回路や操作機構の故障に関する故障。 | Denne feiltyper viser til feil med utløsermekanismen og/eller kontaktbevegelsen. | Ten rodzaj uszkodzenia odnosi się do elektrycznego sterowania i / lub mechanicznego działania wyłącznika | Esta clase de fallo se refiere al control electrico y/o a la operación mecánica del interruptor. | Ova vrsta kvara odnosi se na električno upravljanje i/ili mehanički pogon prekidača. | This kind of failure refers to the electrical control and/or mechanical operation of the circuit breaker. | Acest tip de defectare se refera la controlul electric sau/si actionarea mecanica a intreruptorului. | X | X
[15 empty] | X | X
2.7 | Closes without command; Opens without command | 2.7 | Closes without command; Opens without command | Zapnul bez povelu; Vypnul bez povelu | Closes without command; Opens without command | Se ferme sans ordre, S'ouvre sans ordre | Schließt ohne Kommando; öffnet ohne Kommando | 自然投入、自然開放 | Kobler uten å ha fått kommandosignal. | Zamyka się bez podania impulsu; Otwiera się bez podania impulsu | Cierra sin orden; Abre sin orden | Uklapa bez komande; Isklapa bez komande. | Closes without command; Opens without command | Inchide fara comanda; Deschide fara comanda | X | X
| This kind of failure refers to the electrical control and/or operating mechanism of the circuit breaker (not due to failure of the substation protection or control system functions). |  | This kind of failure refers to the electrical control and/or operating mechanism of the circuit breaker (not due to failure of the substation protection or control system functions). | Tento druh poruchy vypovida o elektrickem ovladani nebo o mechanicke funkci vypinace (nikoliv vsak v dusledku poruchy funkce systemu ochran nebo ridiciho systemu v rozvodne) | This kind of failure refers to the electrical control and/or operating mechanism of the circuit breaker (not due to failure of the substation protection or control system functions). | Cette défaillance concerne soit le circuit électrique d'ordres de fermeture / ouverture et/ou le fonctionnement mécanique de la commande du disjoncteur (mais n'est pas dû à une défaillance du système de protection ou de contrôle commande du poste). | Dieser Fehlertyp bezieht sich auf die elektrische Steuerung und/oder den mechanischen Betrieb des Leistungsschalters (nicht durch Fehler des Anlagenschutzes oder der Anlagensteuerung) | 遮断器の電気的な制御回路や操作機構の故障に関する故障。（ただし、変電所の保護システムや制御回路の故障は除く。） | Denne feiltyper viser til feil med utløsermekanismen og/eller kontaktbevegelsen, ikke til feil med vernet et kontrollanlegget på stasjonen. | Ten rodzaj uszkodzenia odnosi się do elektrycznego sterowania i / lub napędu wyłącznika (a nie do uszkodzenia układów zabezpieczeń i sterowania stacji. | Esta clase de fallo se refiere al control electrico y/o al mecanismo de operación del interruptor (no debido a fallo de las protecciones de la subestación o del sistema de control) | Ova vrsta kvara odnosi se na električno upravljanje i/ili pogonski mehanizam prekidača (ne na kvar zaštite ili upravljanja postrojenja). | This kind of failure refers to the electrical control and/or operating mechanism of the circuit breaker (not due to failure of the substation protection or control system functions). | Acest tip de defectare se refera la controlul electric si/sau actionarea mecanica a intreruptorului (nu se datoreaza defectarii protectiei statiei sau functiilor sistemului de control). | X | X
[15 empty] | X | X
2.8 | Fails to carry current | 2.8 | Fails to carry current | Neprenesl proud | Fails to carry current | Défaillance dans le transite du courant | Führt den Strom nicht | 通電異常 | Greier ikke å føre strøm i innkoblet posisjon. | Nie przewodzi prądu. | No conduce corriente | Ne vodi struju | Fails to carry current | Nu conduce curentul | X | X | X
| This kind of failure refers to an electrical phenomena in the interrupter units or terminals of the circuit breaker at the closed position. |  | This kind of failure refers to an electrical phenomena in the interrupter units or terminals of the circuit breaker at the closed position. | Tento druh poruchy vypovida o elektrickem jevu ve vypinacich komorach nebo na primarnim pripojeni vypinace v zapnutem stavu. | This kind of failure refers to an electrical phenomena in the interrupter units or terminals of the circuit breaker at the closed position. | Cette défaillance est relative à un phénomène électrique dans la/les chambres de coupure ou les bornes du disjoncteur en position fermée. | Dieser Fehlertyp bezieht sich auf einen elektrischen Effekt in der Unterbrechereinheit oder den Primäranschlüssen eines Leistungsschalters im eingeschalteten Zustand. | 遮断器が投入状態の時の故障であり、消弧室部品や導体接続部の電気的特性変化に起因する。 | Denne feiltypen viser til elektriske fenomener (varmgang etc.) i brytekammeret eller i bryterens terminaler mens bryteren er innkoblet. | Ten rodzaj uszkodzenia dotyczy elektrycznego zjawiska w komorach gaszących lub zacisków wyłącznika w pozycji zamkniętej. | Esta clase de fallo se refiere a un fenómeno electrico en la unidad de interrupción o en los terminales del interruptor en la posición de cerrado. | Ova vrsta kvara odnosi se na električke pojave u prekidnoj komori i priključnicama prekidača u uklopljenom položaju. | This kind of failure refers to an electrical phenomena in the interrupter units or terminals of the circuit breaker at the closed position. | Acest tip de defectare se refera la un fenomen electric in unitatile de intreruptor sau terminalele intreruptorului in pozitie inchisa. | X | X | X
[15 empty] | X | X | X
2.9 | Breakdown to earth | 2.9 | Breakdown to earth | Jednopolovy zkrat | Breakdown to earth | Défaut à la terre | Durchschlag zur Erde | 対地閃絡 | Overslag til jord. | Przebicie izolacji doziemnej | Defecto a tierra. | Proboj prema zemlji | Breakdown to earth | Punere la pamant | X | X | X | X | X | X
| This kind of failure refers to an electrical breakdown between parts of the circuit breaker at service voltage and earthed parts. |  | This kind of failure refers to an electrical breakdown between parts of the circuit breaker at service voltage and earthed parts. | Tento druh poruchy vypovida o elektrickem preskoku mezi castmi vypinace pod napetim vvn nebo zvn a uzemnenymi castmi nebo zemi | This kind of failure refers to an electrical breakdown between parts of the circuit breaker at service voltage and earthed parts. | Cette défaillance est un franchissement de l'isolement entre les parties du disjoncteur sous tension de service et les pièces reliées à la terre | Dieser Fehlertyp bezieht sich auf einen elektrischen Durchschlag zwischen Teilen des Leistungsschalters auf Hochspannungspotential und geerdeten Teilen. | 課電状態の遮断器の部品と対地間で発生した電気的絶縁破壊。 | Denne feiltypen viser til dielektrisk gjennomslag / overslag mellom deler i bryteren som er på høyspenningspotensial og jordede deler. | Ten rodzaj uszkodzenia dotyczy elektrycznego przebicia pomiędzy częściami znajdującymi się pod napięciem roboczym, a częściami uziemionymi. | Esta clase de fallo se refiere a una falta entre partes del interruptor a la tensión de servicio y partes puestas a tierra. | Ova vrsta kvara odnosi se na električki proboj između dijelova prekidača na pogonskom naponu i uzemljenih dijelova. | This kind of failure refers to an electrical breakdown between parts of the circuit breaker at service voltage and earthed parts. | Acest tip de defectare se refera la o punere la pamant intre partile intreruptorului la tensiunea de serviciu si partile puse la pamant. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
2.10 | Breakdown between poles | 2.10 | Breakdown between poles | Preskok (zkrat) mezi poly | Breakdown between poles | Amorçage entre pôles | Durchschlag zwischen den Polen | 相間閃絡 | Overslag mellom faser. | Przebicie izolacji pomiędzy biegunami | Defecto entre fases. | Proboj između polova | Breakdown between poles | Amorsaj intre poli | X | X | X | X | X | X
| This kind of failure refers to an electrical breakdown between parts at service voltage of different poles of the circuit breaker. |  | This kind of failure refers to an electrical breakdown between parts at service voltage of different poles of the circuit breaker. | Tento druh poruchy vypovida o elektrickem preskoku mezi castmi na napeti vvn nebo zvn ruznych polu vypinace | This kind of failure refers to an electrical breakdown between parts at service voltage of different poles of the circuit breaker. | Cette défaillance se caractérise par un amorçage entre parties sous tension entre deux pôles d'un même disjoncteur. | Dieser Fehlertyp bezieht sich auf einen elektrischen Durchschlag zwischen Teilen auf Hochspannungspotential an unterschiedlichen Polen eines Leistungsschalters . | 課電状態の遮断器部品と他相の遮断器部品の間で発生した電気的絶縁破壊。 | Denne feiltypen viser til dielektrisk gjennomslag / overslag mellom deler som er på høyspenningspotensial tilhørende forskjellige faser i bryteren. | Ten rodzaj uszkodzenia dotyczy elektrycznego przebicia pomiędzy częściami znajdującymi się pod napięciem roboczym różnych biegunów wyłącznika. | Esta clase de fallo se refiere a una falta entre partes en tensión de diferentes fases del interruptor. | Ova vrsta kvara odnosi se na električni proboj između dijelova prekidača na pogonskom naponu ali između različitih polova. | This kind of failure refers to an electrical breakdown between parts at service voltage of different poles of the circuit breaker. | Acest tip de defectare se refera la un amorsaj intre partile la tensiunea de serviciu ale diferitilor poli ai intreruptorului. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
2.11 | Breakdown across pole during operation (Does not make/interrupt the current) | 2.11 | Breakdown across pole during operation (Does not make/interrupt the current) | Vnitrni pruraz mezi kontakty polu behem spinaci operace (nezapnul/nevypnul proud) | Breakdown across pole during operation (Does not make/interrupt the current) | Amorçage entre pôles en fonctionnement (n'établit pas / ne coupe pas le courant) | Durchschlag über einen Pol während einer Schalthandlung ( Schaltet den Strom nicht ein / schaltet den Strom nicht aus) | 動作中の極間閃絡（電流の投入、遮断動作は含まない。） | Overslag over bryterpol under kobling (gfreier ikke å bryte/føre strøm). | Przebicie izolacji bieguna podczas operacji (Nie załacza prądu/ załacza prąd) | Defecto interno a través de un polo durante una operación (Establece o no la corriente) | Proboj na jednom polu za vrijeme rada (Ne uklapa/prekida struju) | Breakdown across pole during operation (Does not make/interrupt the current) | Conturnarea unui pol in timpul unei actionari (Nu stabileste/ nu intrerupe curentul) | X
| This kind of failure refers to an electrical phenomena in the interrupter units of the circuit breaker during making and breaking operations. |  | This kind of failure refers to an electrical phenomena in the interrupter units of the circuit breaker during making and breaking operations. | Tento druh poruchy vypovida o elektrickem jevu ve vypinacich komorach v prubehu zapinaci nebo vypinaci operace | This kind of failure refers to an electrical phenomena in the interrupter units of the circuit breaker during making and breaking operations. | Cette défaillance se caractérise par un problème électrique entre les contacts de la chambre de coupure du disjoncteur pendant une manœuvre d'ouverture ou de fermeture. | Dieser Fehlertyp bezieht sich auf einen elektrischen Effekt in der Unterbrechereinheit eines Leistungsschalters während EIN- oder AUS-Schaltungen. | 開極、閉極動作中の遮断器の消弧室極間部で発生した電気的絶縁破壊。 | Denne feiltypen viser til elektriske feil i brytekammeret under kobling. | Ten rodzaj uszkodzenia dotyczy elektrycznego zjawiska w komorach gaszących wyłącznika podczas operacji załączania i wyłączania prądu. | Esta clase de fallo se refiere a un fenomeno eléctrico en la unidad de interrupción del interruptor durante una operación de establecimiento o corte de corriente. | Ova vrsta kvara odnosi se na električe pojave u prekidnoj komori prekidača za vrijeme sklopnih operacija | This kind of failure refers to an electrical phenomena in the interrupter units of the circuit breaker during making and breaking operations. | Acest tip de defectare se refera la un fenomen electric in unitatile de intrerupere ale unui intreruptor in timpul actionarilor de inchidere si deschidere. | X
X
2.12 | Breakdown across pole in open position | 2.12 | Breakdown across pole in open position | Vnitrni pruraz mezi kontakty ve vypnute poloze | Breakdown across pole in open position | Amorçage entre contacts de la chambre de coupure en position ouverte. | Durchschlag über einen Pol in Ausschaltstellung | 開極状態での極間閃絡 | Overslag over bryterpol i utkoblet stilling. | Przebicie izolacji bieguna w pozycji otwartej | Defecto interno a través de un polo abierto | Proboj na jednom polu u otvorenom položaju | Breakdown across pole in open position | Conturnarea unui pol in pozitie deschisa | X
| This kind of failure refers to an electrical breakdown between the contacts of the interrupter units or the terminals of the circuit breaker within one pole. |  | This kind of failure refers to an electrical breakdown between the contacts of the interrupter units or the terminals of the circuit breaker within one pole. | Tento druh poruchy vypovida o elektrickem prurazu mezi kontakty vypinaci komory nebo mezi primarnimi pripojovacimi misty v jednom polu vypinace | This kind of failure refers to an electrical breakdown between the contacts of the interrupter units or the terminals of the circuit breaker within one pole. | Cette défaillance se caractérise par un amorçage entre les contacts de la chambre de coupure ou entre bornes d'un pôle de disjoncteur. | Dieser Fehlertyp bezieht sich auf einen elektrischen Effekt zwischen den Kontakten der Unterbrechereinheiten oder den Primäranschlüssen eines Leistungsschalters innerhalb eines Pols. | 開極状態の遮断器の導体接続部や消弧室極間で発生した電気的絶縁破壊。 | Denne feiltypen viser til overslag / gjennomslag over kontaktene i bryterkammeret eller terminalene i samme bryterpol. | Ten rodzaj uszkodzenia dotyczy elektrycznego przebicia pomiędzy stykami komór gaszących lub zacisków wyłącznika w jednym biegunie. | Esta clase de fallo se refiere a un defecto entre los contactos de la unidad de interrupción o entre los terminales de un polo del interruptor. | Ova vrsta kvara odnosi se na električki proboj između kontakata u prekidnoj komori ili priključnica prekidača unutar jednog pola. | This kind of failure refers to an electrical breakdown between the contacts of the interrupter units or the terminals of the circuit breaker within one pole. | Acest tip de defectare se refera la o conturnare intre contactele unei unitati de intrerupere sau terminalele unui intreruptor, intr-un pol. | X
X
2.13 | Locking in open or closed position (alarm has been triggered by the control system) | 2.13 | Locking in open or closed position (alarm has been triggered by the control system) | Zablokovani ve vypnute nebo zapnute poloze (signal generovan ridicim systemem) | Locking in open or closed position (alarm has been triggered by the control system) | Blocage en position ouverte ou fermée (l'alarme a été déclenchée par le système de commande) | Gesperrt in AUS oder EIN Schaltstellung (Sperre wurde von der Steuerung gesetzt) | 制御システムによる警報発令 | Låst i utkoblet eller innkoblet stilling (kontrollanlegget har gitt alarm). | Zablokowanie w pozycji otwartej lub zamkniętej (alarm został włączony przez układ sterowania) | Bloqueo en abierto o cerrado (la alarma ha sido activada por el sistema de control) | Blokira u isklopljenom ili uklopljenom položaju (alarm je došao od sistema kontrole) | Locking in open or closed position (alarm has been triggered by the control system) | Blocare in pozitie inchisa sau deschisa (alarma a fost actionata de sistemul de control) | X | X
| This kind of failure refers to an electrical blocking set by the control system of the circuit breaker. The failure characteristic is not meant for situation where the locking is discovered, while giving a command to open or close. In the case the failure mode "does not close or open on command" is applicable. |  | This kind of failure refers to an electrical blocking set by the control system of the circuit breaker. The failure characteristic is not meant for situation where the locking is discovered, while giving a command to open or close. In the case the failure mode "does not close or open on command" is applicable. | Tento druh poruchy vypovida o elektrickem zablokovani funkce vlastnim blokovacim systemem vypinace. Tento druh poruchy se netyka situace, pri niz je zablokovani objeveno az v okamziku vyslani povelu ZAP nebo VYP (porucha typu "nezypnul/nevypnul na povel"). | This kind of failure refers to an electrical blocking set by the control system of the circuit breaker. The failure characteristic is not meant for situation where the locking is discovered, while giving a command to open or close. In the case the failure mode "does not close or open on command" is applicable. | Cette défaillance se caractérise par un blocage électrique du système de commande du disjoncteur. La défaillance n'est pas signalée jusqu'au moment ou la situation est découverte, tout en autorisant un ordre d'ouverture ou de fermeture. Dans ce cas le mode de défaillance "ne se ferme pas ou ne s'ouvre pas sur commande" est applicable. | Dieser Fehlertyp bezieht sich auf eine elektrische Sperre, die von der Steuerung des Leistungsschalters gesetzt wurde. Dieser Fehlertyp beschreibt nicht die Situation wenn die Blockierung erst beim geben eines EIN- oder AUS-Kommandos entdeckt wird. In diesem Fall ist der Fehlertyp "Schließt nicht auf Kommando; öffnet nicht auf Kommando" anzuwenden. | 遮断器の制御システムの電気的鎖錠装置に関する故障。その故障の特徴は、鎖錠が発見された部位や開閉極指令を与える状態とは無関係であることである。その場合の故障モードは、”開閉極不能”が適用される。 | Denne feiltypen angir når bryterens utløsermekanisme har "låst seg". Denne feiltypen er ikke ment å omfatte situasjoner når blokkeringen er oppdaget i forbindelse med koblinger. I såfall er feiltypen "Kobler ikke på kommando". | Ten rodzaj uszkodzenia dotyczy elektrycznego blokowania przez układ sterowania wyłącznika. Uszkodzenie to nie dotyczy sytuacji w której blokowanie zostało stwierdzone podczas podawania impulsu sterowaniczego na otwarcie lub zamknięcie. W takim przypadku jest to tryb uszkodzenia "nie zamyka się lub otwiera po podaniu impulsu sterowaniczego". | Esta clase de fallo se refiere a un bloqueo eléctrico establecido por el sistema de control del interruptor. Este fallo característico no es aplicable a situaciones, donde el bloqueo es descubierto mientras se da una orden de apertura o cierre. En ese caso, el tipo de fallo es "No abre o no cierra a la orden" | Ova vrsta kvara odnosi se na električne blokade i kontrolu prekidača. Ne radi se o kvaru koji je uočen za vrijeme sklopnih operacija. Tada se primjenjuje kvar "ne uklapa/isklapa na komandu". | This kind of failure refers to an electrical blocking set by the control system of the circuit breaker. The failure characteristic is not meant for situation where the locking is discovered, while giving a command to open or close. In the case the failure mode "does not close or open on command" is applicable. | Acest tip de defectare se refera la o blocare electrica actionata de sistemul de control al intreruptorului. Aceasta defectare caracteristica nu se aplica in situatia cand blocarea este depistata in momentul cand se da o comanda de deschidere sau inchidere. In acest caz modul de defectare aplicabil este "nu inchide sau nu deschide la comanda". | X | X
[15 empty] | X | X
2.14 | Locking in open or closed position | 2.14 | Locking in open or closed position | Zablokovani ve vypnute nebo zapnute poloze | Locking in open or closed position | Blocage en position Ouverte ou Fermée | Sperre in AUS- oder EIN-Schaltstellung | 開極、閉極状態での鎖錠。 | Låst i utkoblet eller innkoblet stilling | Zablokowanie w pozycji otwartej lub zamkniętej | Bloqueo en abierto o cerrado | Blokira u isklopljenom ili uklopljenom položaju | Locking in open or closed position | Bocare in pozitie deschisa sau inchisa | X | X
| This kind of failure refers to an electrical blocking set by the control system of the circuit breaker. |  | This kind of failure refers to an electrical blocking set by the control system of the circuit breaker. | Tento druh poruchy vypovida o elektrickem zablokovani funkce vlastnim blokovacim systemem vypinace. | This kind of failure refers to an electrical blocking set by the control system of the circuit breaker. | Cette défaillance se caractérise par un blocage électrique du système de commande du disjoncteur. | Dieser Fehlertyp bezieht sich auf eine elektrische Sperre, die durch die Steuerung des Leistungsschalters gesetzt wurde. | 遮断器の制御システムの電気的鎖錠装置に関する故障。 | Denne feiltypen angir når bryterens utløsermekanisme har "låst seg" | Ten rodzaj uszkodzenia dotyczy elektrycznej blokady spowodowanej przez układ sterowania wyłącznika | Esta clase de fallo se refiere a un bloqueo eléctrico establecido por el sistema de control del interruptor. | Ova vrsta kvara odnosi se na električne blokade i kontrolu prekidača. | This kind of failure refers to an electrical blocking set by the control system of the circuit breaker. | Acest tip de defectare se refera la o blocare electrica data de sistemul de control al intreruptorului. | X | X
| This failure characteristic is not meant for situations, where the locking is discovered, while giving a command to open or to close. I that case the failure mode “Does not close or open on command” is applicable. |  | This failure characteristic is not meant for situations, where the locking is discovered, while giving a command to open or to close. I that case the failure mode “Does not close or open on command” is applicable. | Tento druh poruchy se netyka situace, pri niz je zablokovani objeveno az v okamziku vyslani povelu ZAP nebo VYP (porucha typu "nezypnul/nevypnul na povel"). | This failure characteristic is not meant for situations, where the locking is discovered, while giving a command to open or to close. I that case the failure mode “Does not close or open on command” is applicable. | Cette défaillance ne sera pas signalée pour les situations, où le blocage est découvert, alors que l'on donne un ordre d'ouverture ou de fermeture. Dans ce cas le mode de défaillance "ne se ferme pas ou s'ouvre sur commande" est applicable. | Diese Fehlerart trifft nicht für Fälle zu, bei denen die Sperre erst während der Kommandogabe für eine EIN- oder AUS-Schaltung bemerkt wird. In diesen Fällen ist der Fehlertyp "Schließt nicht auf Kommando; öffnet nicht auf Kommando" zu wählen. | その故障の特徴は、鎖錠が発見された部位や開閉極指令を与える状態とは無関係であることである。その場合の故障モードは、”開閉極不能”が適用される。 | Denne feiltypen angir når bryterens utløsermekanisme har "låst seg". Denne feiltypen er ikke ment å omfatte situasjoner når blokkeringen er oppdaget i forbindelse med koblinger. I såfall er feiltypen "Kobler ikke på kommando". | Ta cecha uszkodzenia nie oznacza sytuacji, w której zablokowanie zostało stwierdzone, podczas podania impulsu na otwarcie lub zamknięcie. W takim przypadku ma zastosowanie rodzaj uszkodzenia "Nie zamyka się lub nie otwiera po podaniu impulsu sterowania". | Este fallo característico no es aplicable a situaciones, donde el bloqueo es descubierto mientras se da una orden de apertura o cierre. En ese caso, el tipo de fallo es "No abre o no cierra a la orden" | Karakteristika ovog kvara ne odnosi se na situacije kada je blokiranje uočeno za vrijeme sklopnih operacija. Tada se primjenjuje kvar "ne uklapa/isklapa na komandu". | This failure characteristic is not meant for situations, where the locking is discovered, while giving a command to open or to close. I that case the failure mode “Does not close or open on command” is applicable. | Aceasta defectare caracteristica nu se aplica in situatia cand blocarea este depistata in momentul cand se da o comanda de deschidere sau inchidere. In acest caz modul de defectare aplicabil este "nu inchide sau nu deschide la comanda". | X | X
[15 empty] | X | X
2.15 | Main Kind of Service | 2.15 | Main Kind of Service | Hlavni typ provozu | Main Kind of Service | Principale classification d'application | Haupt-Schaltaufgabe im Betrieb | 主要な運用条件 | Vanligste koblingstype | Podstawowy rodzaj pracy | Función principal | Glavna vrsta pogona | Main Kind of Service | Tipul principal al serviciului | X
| The predominant fault operating service. For a breaker-and-a-half scheme protecting both a transformer and a line, the main kind of service will be line protection since the majority of fault interruptions are associated with line faults. |  | The predominant fault operating service. For a breaker-and-a-half scheme protecting both a transformer and a line, the main kind of service will be line protection since the majority of fault interruptions are associated with line faults. | Prevladajici typ provozu pri vypinani zkratu v siti. U vypinace ve schematu jeden a pul vypinace na odbocku, ktery chrani jak vedeni tak i transformator, bude hlavnim typem provozu ochrana vedeni, protoze vetsina poruchovych vypnuti je spojena s poruchami vedeni. | The predominant fault operating service. For a breaker-and-a-half scheme protecting both a transformer and a line, the main kind of service will be line protection since the majority of fault interruptions are associated with line faults. | La classification prédominante des défauts en service. Pour un schéma 1 disjoncteur et 1/2 protégeant soit un transformateur soit une ligne, la classification principale sera, protection de ligne puisque la majorité de interruptions de défaut sont associées à la ligne. | Die überwiegende Schaltaufgabe im Fehlerfall. Eine Anderthalb-Leistungsschalter-Anordnung mit der Schutzaufgabe sowohl Transformator als auch Freileitung wird überwiegend zum Leitungsschutz eingesetzt werden, da die meisten Fehler auf Freileitungen auftreten. | 主要な事故除去操作の運用条件。例えば変圧器回線や架空線路回線の保護のために１・１／２遮断方式を採用した場合、大部分の事故遮断は架空線路での事故除去のために行われるため、主要な運用条件は架空線路保護となると考えられる。 | Den vanligst forekommende koblingstype ved koblinger i forbindelse med feil. For brytere som kobler både transformator og linje, vil vanligste koblingstype være linje siden mesteparten av koblingene vil være linjeutkoblinger. | Dominująca praca dotyczy likwidacji zwarć. Dla wyłączników w układzie półtora wyłącznikowym chroniącego zarówno transformator jak i linię, podstawowym rodzajem pracy będzie ochrona linii, ponieważ większość wyłączeń zwarciowych jest związana likwidacją zwarć na linii. | Función predominante en la falta. Para un esquema de interruptor y medio con transformador y línea, la función principal será la de línea, ya que la mayoria de las interrupciones por falta estan relacionadas con faltas en la línea. | Vrsta pogona koja je prethodila kvaru. | The predominant fault operating service. For a breaker-and-a-half scheme protecting both a transformer and a line, the main kind of service will be line protection since the majority of fault interruptions are associated with line faults. | Serviciul predominant cu defecte de exploatare. Pentru o schema cu un intreruptor jumatate protejand atat un trafo cat si o linie, tipul principal al serviciului este protejarea liniei, deoarece majoritatea intreruperilor in urma defectelor este asociata cu defectele LEA. | X
X
2.16 | Mechanisms | 2.16 | Mechanisms | Pohon | Mechanisms | Mécanismes | Antriebsarten | 操作機構 | Driftsanordninger | Napęd | Mecanismos de accionamiento Mechanisms (DEFINITIONS ARE MISSING) | Mehanizam | Mechanisms | Mecanism | X | X
| Hydraulic (may include springs) |  | Hydraulic (may include springs) | Hydralicky (muze obsahovat pruziny) | Hydraulic (may include springs) | Hydraulique (peut inclure des ressorts) | Hydraulik (kann Federn enthalten) | 油圧操作機構（ばね操作機構を併用する場合あり） | Hydraulisk (kan inkludere fjærer) | Hydrauliczny (może zawierać sprężyny) | Hidráulico (puede incluir resortes) | Hidraulički (može imati i opruge) | Hydraulic (may include springs) | Hidraulic (poate include resoarte) | X | X
| Operating mechanism where the force for opening or closing operation, or both, is generated by hydraulic pressure. Springs may be used for opening operations in case of hydraulic closing operations, or for closing operations in case of hydraulic opening operations. |  | Operating mechanism where the force for opening or closing operation, or both, is generated by hydraulic pressure. Springs may be used for opening operations in case of hydraulic closing operations, or for closing operations in case of hydraulic opening operations. | Sila pro ZAP nebo VYP nebo ZAP i VYP je generovana hydraulickym tlakem (pružiny mohou být použity pro ZAP nebo VYP pri hydralickem VYP nebo ZAP) | Operating mechanism where the force for opening or closing operation, or both, is generated by hydraulic pressure. Springs may be used for opening operations in case of hydraulic closing operations, or for closing operations in case of hydraulic opening operations. | Mécanisme où la force pour l'ouverture ou la fermeture, ou les deux, est produite par une pression hydraulique. Des ressorts peuvent être utilisés pour l'ouverture avec une fermeture hydraulique, ou pour la fermeture avec une ouverture hydraulique. | Antrieb, bei dem die Kraft für die AUS- und/oder EIN-Schaltung durch Hydraulikdruck erzeugt wird. Bei hydr. EIN-Schaltung oder hydr. AUS-Schaltung können Federn für die AUS- bzw. EIN-Schaltung verwendet sein. | 油圧によって開極操作、閉極操作もしくはその両方を行うための操作力を発生する操作機構。閉極操作を油圧操作、開極操作をばね操作で行う場合、またその逆に、開極操作を油圧操作、閉極操作をばね操作機構で行う場合もある。 | Driftsanordning der kraften til inn- og/eller utkobling kommer fra et hydraulikktrykk. Fjærer kan være anvendt ved utkobinger når hydraulikken sørger for innkobling, og vise versa. | Napęd, w którym siła potrzebna do wykonania operacji otwierania lub zamykania lub obu tych operacji, jest generowana przez ciśnienie hydrauliczne. Sprężyny mogą być używane do operacji otwierania w przypadku hydraulicznej operacji zamykania lub do operacji zamykania w przypadku hydraulicznej operacji zamykania. | Mecanismo de operación en el que la fuerza para las maniobras de apertura y/o cierre, es suministrada por una presión hidráulica. Incluyendo los mecanismos que utilizan resortes para maniobras de apertura cuando para el cierre se utiliza mando hidráulico o los que utilizan resortes para maniobras de cierre cuando para la apertura se utiliza mando hidráulico. | Pogonski mehanizam kod kojeg se sila za otvaranje i/ili zatvaranje dobija pomoću hidrauličkog tlaka. Opruga se može koristiti za otvaranje u slučaju hidrauličkog zatvaranja, ili za zatvaranje u slučaju hidrauličkog otvaranja. | Operating mechanism where the force for opening or closing operation, or both, is generated by hydraulic pressure. Springs may be used for opening operations in case of hydraulic closing operations, or for closing operations in case of hydraulic opening operations. | Mecanismul de actionare la care forta pt. actionarea de deschidere sau inchidere este generata de presiunea hidraulica. Resoartele pot fi utilizate pt. operatia de deschidere in cazul operatiei hidraulice de inchidere, sau pentru operatia de inchidere in cazul actionarilor hidraulice de deschidere. | X | X
| Pneumatic (may include springs) |  | Pneumatic (may include springs) | Tlakovzdusny (muze obsahovat pruziny) | Pneumatic (may include springs) | Pneumatique (peut inclure des ressorts) | Druckluft (kann federn enthalten) | 空気操作機構 (ばね操作機構を併用する場合あり) | Pneumatisk (som kan inkluderer fjærer) | Pneumatyczny (może zawierać sprężyny) | Neumático (puede incluir resortes) | Pneumatski (može imati i opruge) | Pneumatic (may include springs) | Pneumatic (poate include resoarte) | X | X
| Operating mechanism where the force for opening or closing operation, or both, is generated by pneumatic pressure. Springs may be used for opening operations in case of pneumatic closing operations, or for closing operations in case of pneumatic opening operations. |  | Operating mechanism where the force for opening or closing operation, or both, is generated by pneumatic pressure. Springs may be used for opening operations in case of pneumatic closing operations, or for closing operations in case of pneumatic opening operations. | Sila pro ZAP nebo VYP nebo ZAP i VYP je generovana tlakem vzduchu (pružiny mohou být použity pro ZAP nebo VYP pri tlakovzdusnem VYP nebo ZAP) | Operating mechanism where the force for opening or closing operation, or both, is generated by pneumatic pressure. Springs may be used for opening operations in case of pneumatic closing operations, or for closing operations in case of pneumatic opening operations. | Mécanisme où la force pour l'ouverture ou la fermeture, ou les deux, est produite par une pression pneumatique. Des ressorts peuvent être utilisés pour l'ouverture avec une fermeture pneumatique, ou pour la fermeture avec une ouverture pneumatique. | Antrieb, bei dem die Kraft für die AUS- und/oder EIN-Schaltung durch Druckluft erzeugt wird. Bei pneumatischer EIN-Schaltung oder pneumatischer AUS-Schaltung können Federn für die AUS- bzw. EIN-Schaltung verwendet sein. | 空気圧によって開極操作、閉極操作もしくはその両方を行うための操作力を発生する操作機構。閉極操作を空気操作、開極操作をばね操作で行う場合、またその逆に、開極操作を空気操作、閉極操作をばね操作機構で行う場合もある。 | Driftsanordning der kraften til inn- og/eller utkobling genereres av trykkluft. Fjærer kan være anvendt ved utkobinger når trykkluften sørger for innkobling, og vise versa. | Napęd, w którym siła potrzebna do wykonania operacji otwierania lub zamykania lub obu tych operacji, jest generowana przez ciśnienie pneumatyczne. Sprężyny mogą być używane do operacji otwierania w przypadku pneumatycznej operacji zamykania lub do operacji zamykania w przypadku pneumatycznej operacji zamykania. | Mecanismo de operación en el que la fuerza para las maniobras de apertura y/o cierre, es suministrada por una presión neumática. Incluyendo los mecanismos que utilizan resortes para maniobras de apertura cuando para el cierre se utiliza mando neumático o los que utilizan resortes para maniobras de cierre cuando para la apertura se utiliza mando neumático. | Pogonski mehanizam kod kojeg se sila za otvaranje i/ili zatvaranje dobija pomoću tlaka zraka. Opruga se može koristiti za otvaranje u slučaju pneumatskog zatvaranja, ili za zatvaranje u slučaju pneumatskog otvaranja. | Operating mechanism where the force for opening or closing operation, or both, is generated by pneumatic pressure. Springs may be used for opening operations in case of pneumatic closing operations, or for closing operations in case of pneumatic opening operations. | Mecanismul de actionare la care forta pt. actionarea de deschidere sau inchidere, sau pentru ambele, este generata de presiunea pneumatica. Resoartele pot fi utilizate pt. operatia de deschidere in cazul operatiilor pneumatice de inchidere, sau pentru operatia de inchidere in cazul operatiilor pneumatice de deschidere. | X | X
| Spring |  | Spring | Pruzinovy | Spring | Ressort | Feder | ばね操作機構 | Fjær | Sprężynowy | Resortes | Opružni | Spring | Resoarte | X | X
| Operating mechanism where the force for opening and closing operations is generated solely by springs. |  | Operating mechanism where the force for opening and closing operations is generated solely by springs. | Sila pro ZAP i VYP je generovana v pouze v mechanickych pruzinach | Operating mechanism where the force for opening and closing operations is generated solely by springs. | Mécanisme où la force pour l'ouverture et la fermeture est produite seulement par des ressorts. | Antrieb, bei dem die Kraft für die AUS- und/oder EIN-Schaltung ausschließlich durch Federn erzeugt wird | ばねによって開極操作、閉極操作を行うための操作力を発生する操作機構。 | Driftsanordning der kraften til inn- og utkobling genereres av fjærer alene. | Napęd, w którym siła potrzebna do wykonania operacji otwierania, jest generowana wyłącznie przez sprężyny. | Mecanismo de operación en el que la fuerza para las maniobras de apertura y cierre, es suministrada únicamente por resortes. | Pogonski mehanizam kod kojeg se sila za otvaranje i/ili zatvaranje dobija isključivo pomoću opruga. | Operating mechanism where the force for opening and closing operations is generated solely by springs. | Mecanism de actionare la care forta pentru actionarile de deschidere sau inchidere este generata numai de resoarte. | X | X
| Other (magnetic, motor, etc.) |  | Other (magnetic, motor, etc.) | Jiny (magneticky, motorovy, a pod.) | Other (magnetic, motor, etc.) | Autre (magnétique, moteur, etc.…) | Andere (z.B. Magnetisch, Motor, etc.) | その他 (磁力、モーターなど) | Annet (magnetisk, motor, ertc.) | Inny (magnetyczny, silnikowy itp.) | Otros (magnetico, motor, etc...) | Drugo (magnetski, elektromotorni itd.) | Other (magnetic, motor, etc.) | Altul (magnetic, motor etc) | X | X
| Operating mechanism where the force for opening and closing operations is generated by other means than hydraulic or pneumatic pressure or springs. Examples are magnetic actuators, or directly connected electric motors. |  | Operating mechanism where the force for opening and closing operations is generated by other means than hydraulic or pneumatic pressure or springs. Examples are magnetic actuators, or directly connected electric motors. | Sila pro ZAP i VYP je generovana jinym zpusobem nez je hadraulicky nebo pneumaticky tlak nebo pruzina (napr. magneticky pohon nebo primo pripojeny elektricky motor) | Operating mechanism where the force for opening and closing operations is generated by other means than hydraulic or pneumatic pressure or springs. Examples are magnetic actuators, or directly connected electric motors. | Mécanisme où la force pour l'ouverture et la fermeture est produite par d'autres moyens que la pression hydraulique ou pneumatique ou des ressorts. Par exemples, un actuacteur magnétique, ou un moteur électrique directement relié à la chambre de coupure. | Antrieb, bei dem die Kraft für die AUS- und/oder EIN-Schaltung durch andere Mittel als Hydraulik- oder Luftdruck oder Federn erzeugt wird. Beispiele sind magnetische Antriebe oder direkt angeflanschte elektr. Motoren. | 開極操作、閉極操作を行うための操作力を油圧、空気圧、ばね力以外の手段で発生する操作機構。（例:磁気駆動､電気モーターなど） | Driftsanordning der kraften til inn- og utkobling ikke er genereret av hydraulikk, trykkluft eller fjærer. Eksempler på slike er magnetiske aktuatorer og direkte tilkoblede motorer. | Napęd, w którym siła potrzebna do wykonania operacji otwierania lub zamykania jest generowana w inny sposób niż przez ciśnienie hydrauliczne, pneumatyczne, sprężyny. Przykładem są siłowniki magnetyczne lub bezpośrednio sprzęgnięty z napędem silnik elektryczny. | Mecanismo de operación en el que la fuerza para las maniobras de apertura y cierre, es suministrada por otros medios distintos a presiones hidráulicas o neumáticas o resortes. Algunos ejemplos son los actuadores magnéticos o motores eléctricos. | Pogonski mehanizam kod kojeg se sila za otvaranje i/ili zatvaranje ne dobija pomoću hidrauličkog ili pneumatskog tlaka, odnosno opruga. Primjeri su magnetski pobuđivači ili direktan priključak električnih motora. | Operating mechanism where the force for opening and closing operations is generated by other means than hydraulic or pneumatic pressure or springs. Examples are magnetic actuators, or directly connected electric motors. | Mecanism de actionare la care forta pentru actionarile de deschidere sau inchidere este generata prin alte mijloace decat presiunea hidraulica sau pneumatica sau resoarte. Exemplu sunt servomotoarele magnetice sau motoare electrice conectate direct. | X | X
[15 empty] | X | X
[15 empty] | X | X
2.17 | Circuit breaker bay (CB-bay) | 2.17 | Circuit breaker bay (CB-bay) | Pocet vypinacovych poli (3-fazove) | Circuit breaker bay (CB-bay) | Travée disjoncteur | Leistungsschalterfeld (CB-bay) | 遮断器回線 (CB回線) | Effektbryterfelt | Pole wyłącznikowe | Posición de interruptor (CB-bay) | Br. prekidačkih polja (3-fazno) | Circuit breaker bay (CB-bay) | Celula cu intreruptor | X
| A three phase assembly consisting of one circuit breaker or switch, its associated disconnectors, instrument transformers, interconnecting busducts up to and including the line disconnect switch (if applicable), and the section of main busbar (if applicable). |  | A three phase assembly consisting of one circuit breaker or switch, its associated disconnectors, instrument transformers, interconnecting busducts up to and including the line disconnect switch (if applicable), and the section of main busbar (if applicable). | Vypinacove pole je 3-fazova sestava, ktera se sklada z vypinace, s nim sousedicich odpojovacu, pristrojovych transformatoru, uzemnovacu, propojovacich vedeni mezi nimi az k vyvodovymi odpojovacum (jsou-li pouzity) a z casti hlavnich pripojnic nebo pomocne pripojnice (je-li pouzita). Pocet vypinacovych poli v ZRZ je roven poctu vypinacu v ZRZ. | A three phase assembly consisting of one circuit breaker or switch, its associated disconnectors, instrument transformers, interconnecting busducts up to and including the line disconnect switch (if applicable), and the section of main busbar (if applicable). | Ensemble triphasé composé d'un disjoncteur ou interrupteur, des sectionneurs associés, des transformateurs de mesure, des liaisons d'interconnexion reliant ensemble les sectionneurs de ligne (si applicable), et les jeux de barres principaux (si applicable) | Eine dreiphasige Anordnung, die aus einem Leistungs- oder Lastschalter, zugehörigen Trennschaltern, Wandlern, Verbindungsbausteinen sowie einschließlich dem Leitungstrennschalter und zugehörigen Abschnitt der Sammelschiene (wenn zutreffend) besteht. | 1台の遮断器もしくは開閉器からなる3相1組の回線。この１回線に遮断器の他に断路器、接地開閉器、母線連絡部が含まれており、運用条件によって、送電線用断路器や主母線連絡部も適用される。 | En trefase enhet bestående av en effektbryter med tilhørende skillebrytere, måletransformatorer, lederseksjoner. | Pole wyłącznikowe zespołem składającym się z jednego wyłącznika i towarzyszących mu odłączników | Conjunto trifásico consistente en un interruptor, sus seccionadores asociados, transformadores de medida y protección, conductos de interconexión y seccionadores de línea (si aplica) y la parte de la barra principal (si aplica). | Prekidačko polje je trofazni modul koji se sastoji od jednog prekidača, pripadajućih rastavljača, mjernih transformatora, spojnih sabirnica pa sve do i uključujući zemljospojnik. Broj prekidačkih polja u postrojenju jednak je broju prekidača. | A three phase assembly consisting of one circuit breaker or switch, its associated disconnectors, instrument transformers, interconnecting busducts up to and including the line disconnect switch (if applicable), and the section of main busbar (if applicable). | Un ansamblu trifazat constand dintr-un intreruptor, separatoarele asociate, transformatoarele de masura, barele cu conexiunile respective, pana la separatorul de linie (daca este cazul). | X
| Note: |  | Note: | Poznamka : | Note: | Note: | Anmerkung: | 注記： | Note: | Uwaga: | Nota: | Napomena: | Note: | Nota: | X
| One exit bay can consist of more than only one CB-bays, e.g. single line diagram with 1.5 circuit breakers per exit consists of 3 CB-bays per one diameter, single line diagram with two breakers for an exit consists of 2 CB-bays. |  | One exit bay can consist of more than only one CB-bays, e.g. single line diagram with 1.5 circuit breakers per exit consists of 3 CB-bays per one diameter, single line diagram with two breakers for an exit consists of 2 CB-bays. | Jeden vyvod muze obsahovat vice nez pouze jedno vypinacove pole, napr. jednopolove schema s jednim a pul vypinacem na odbocku se sklada ze 3 vypinacovych poli na jednu vetev, jednopolove schema se 2 vypinaci ne odbocku obsahuje 2 vypinacova pole na jeden vyvod. | One exit bay can consist of more than only one CB-bays, e.g. single line diagram with 1.5 circuit breakers per exit consists of 3 CB-bays per one diameter, single line diagram with two breakers for an exit consists of 2 CB-bays. | Certaine travée de départ, peut comporter plus de sous ensemble qu'une travée disjoncteur, par exemple pour un schéma 1Dj et 1/2 disjoncteur par départ, il y a 3 disjoncteurs pour un diamètre, pour un schéma avec deux disjoncteurs par départ, il y a 2 CB-bays. | Ein Abgangsfeld kann aus mehr als nur einem Leistungsschalterfeld bestehen. Z.B. bei 11/2 Leistungsschalteranordnung sind 3 CB-bays vorhanden, bei Abgängen mit zwei Leistungsschaltern sind 2 CB-bays zu werten. | １つの引出し回線は、１台以上のＣＢ回線から構成される場合がある。例：１・１／２遮断方式の単線結線図では３ＣＢ回線、２遮断方式の単線結線図では２ＣＢ回線としてカウントされる。 | En avgang kan bestå av mer enn ett effektbryterfelt, eksempelvis når dobbeltbryterkonfigurasjon. | Jedno pole odejściowe może zawierać więcej niż jedno pole wyłącznikowe np. dla układu 1,5 wyłącznika pole odejściowe zawiera 3 pola wyłącznikowe w jednej gałęzi, a dla układu 2 wyłącznikowego pole odejściowe zawiera 2 pola wyłącznikowe | Una posición de salida puede consistir en más de una única posición de interruptor, p.e. en un diagrama unifilar con 1,5 interruptores por salida consiste en 3 posiciones de interruptor por calle, en un diagrama unifilar con dos interruptores por salida consiste en 2 posiciones de interruptor. | Jedno izlazno polje može sadržavati i više od jednog prekidača, npr. u konfiguraciji 1.5 prekidač po polju sadrži 3 prekidača. | One exit bay can consist of more than only one CB-bays, e.g. single line diagram with 1.5 circuit breakers per exit consists of 3 CB-bays per one diameter, single line diagram with two breakers for an exit consists of 2 CB-bays. | O celula de plecare poate consta din mai mult decat o singura celula cu intreruptor, de exemplu schema monofilara cu 1,5 intreruptoare pe circuit consta in trei celule cu intreruptor pe un diametru, schema monofilara cu 2 intreruptoare pe circuit consta din 2 celule cu intreruptor. | X
X
6.4 | Component | 6.4 | Component | Soucast | Component | Composant | Komponente | 構成機器 | Komponent / del | Element rozdzielnicy | Componente | Komponenta | Component | Componenta | X | X | X | X | X | X
| IEC 60517 |  | IEC 60517 | [11 empty] | X | X | X | X | X | X
| Essential part of the main or earthing circuits of GIS which serves a specific function (e.g. circuit breakers, disconnector, earthing switch, instrument transformer, bushings, busbar, bushing, termination, etc.). |  | Essential part of the main or earthing circuits of GIS which serves a specific function (e.g. circuit breakers, disconnector, earthing switch, instrument transformer, bushings, busbar, bushing, termination, etc.). | Zakladni cast hlavniho nebo uzemnovaciho obvodu ZRZ, ktera slouzi urcitemu specifikovanemu ucelu (napr. vypinac, odpojovac, uzemnovac, pristrojovy transformator, pruchodky, pripojnice, propojeni, koncovka, a pod.) | Essential part of the main or earthing circuits of GIS which serves a specific function (e.g. circuit breakers, disconnector, earthing switch, instrument transformer, bushings, busbar, bushing, termination, etc.). | Pièce essentielle du circuit primaire sous tension et du circuit relié à la terre des GIS, qui assurent une fonction spécifique (par exemple disjoncteurs, sectionneurs, sectionneur de MALT, transformateur de mesure, les traversées, les jeux de barres, etc.). | Wesentlicher Teil des Haupt- oder Erdungskreises einer GIS welcher eine spezifische Funktion beinhaltet (z.B. Leistungsschalter, Trennschalter; Erdungsschalter, Wandler; Durchführungen, Sammelschiene, Anschlüsse, etc.) | 特定の機能を供給するＧＩＳの主回路もしくは接地回路の基本部位。（例：遮断器、断路器、接地開閉器、計器用変成器、ブッシング、母線、端末部品など。） | Selvstendig del av hovedkretsen eller jordsystemet som har sin egen funksjon, eksempelvis effektbryter, skillebryter, jordslutter, samleskinne etc. | Zasadnicza część głównego lub uziemionego obwodu GIS, która służy określonej funkcji (np. wyłączniki, odłączniki, uziemniki, przekładniki, izolatory przepustowe, szyny zbiorcze, głowice kablowe, itp.) | Parte esencial del circuito principal o del circuito de tierra de la subestación blindada el cual realiza una función específica (p.e. Interruptores, seccionadores, seccionadores de p.a.t., transformadores de medida y protección, bornas, barras, botellas terminales, etc.) | Osnovni dio glavnog strujnog kruga ili kruga uzemljenja u GIS-u koji obavlja specifičnu funkciju (npr. prekidač, rastavljač, zemljospojnik, mjerni transformator, provodni izolator, sabirnica, priključnice itd.). | Essential part of the main or earthing circuits of GIS which serves a specific function (e.g. circuit breakers, disconnector, earthing switch, instrument transformer, bushings, busbar, bushing, termination, etc.). | Partea esentiala a circuitelor principale sau de legare la pamant a GIS, care indeplineste o functie specifica (ex. intreruptoare, separatoare, CLP, trafo masura, treceri izolate, bare, terminale etc.) | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
6.5 | Type of enclosure | 6.5 | Type of enclosure | Typ zapouzdreni | Type of enclosure | Type d'enveloppe | Art der Kapselung | 圧力容器の種類 | Kapsling | Rodzaj obudowy | Tipo de envolvente | Tip kučišta | Type of enclosure | Tipul carcasei | X
| Identification of HV conductors number placed in one component enclosure. The components can be either single phase or three phased enclosed |  | Identification of HV conductors number placed in one component enclosure. The components can be either single phase or three phased enclosed | Identifikace poctu vodicu vvn nebo zvn umistenych v jednom pouzdre dane soucasti. Soucasti mohou byt bud 1-polove nebo 3-polove zapouzdrene. | Identification of HV conductors number placed in one component enclosure. The components can be either single phase or three phased enclosed | Nombre de conducteurs HT placés dans une enveloppe. Les composants peuvent être ou monophasés ou triphasés | Identifikation der in einem Gehäuse befindlichen Hochspannungsleiter. Die Komponente kann entweder einphasig oder dreiphasig gekapselt sein. | １つの圧力容器内の高電圧導体の本数の分類。その構成は、相分離と三相一括とに分類される。 | Angivelse av antall faseledere som finnes inne i samme kapsling (enten en eller tre). | Identyfikacja liczby przewodów WN umieszczonych w jednej obudowie szyn. Element szyn może być umieszczony w obudowie jednofazowej lub trójfazowej. | Numero de identificación de los conductores de alta tensión situado en la envolvente del componente. El componente puede ser también de envolvente unipolar o trifásica. | Identifikacija VN vodiča smještenih u sabirničko kučište. Sabirničko kučište može biti jedno-fazno ili tro-fazno oklopljeno. | Identification of HV conductors number placed in one component enclosure. The components can be either single phase or three phased enclosed | Identificarea numarului de conductoare de IT plasate intr-o carcasa. Componentele pot fi anvelopate monofazat sau trifazat. | X
| Type of busbar enclosure |  | Type of busbar enclosure | Typ zapouzdreni pripojnic | Type of busbar enclosure | Type d'enveloppe jeu de barres | Art der Sammelschienenkapselung | 母線の圧力容器の分類 | Samleskinnekapsling | Rodzaj obudowy pola wyłącznikowego | Tipo de envolvente de las barras | Tip sabirničkog kučišta | Type of busbar enclosure | Tipul carcasei de bara | X
| Identification of HV conductors number placed in one busbar enclosure. The busbar component can be either 1 phase enclosed or 3 phase enclosed. |  | Identification of HV conductors number placed in one busbar enclosure. The busbar component can be either 1 phase enclosed or 3 phase enclosed. | Identifikace poctu vodicu vvn nebo zvn umistenych v jednom pouzdre pripojnic. Pripojnice mohou byt bud 1-polove nebo 3-polove zapouzdrene. | Identification of HV conductors number placed in one busbar enclosure. The busbar component can be either 1 phase enclosed or 3 phase enclosed. | Nombre de conducteurs HT placés dans une enveloppe de jeu de barres. Les composants peuvent être ou monophasés ou triphasés | Identifikation der in einem Sammelschienengehäuse befindlichen Hochspannungsleiter. Die Sammelschienenkomponente kann entweder einphasig oder dreiphasig gekapselt sein. | １つの母線の圧力容器内の高電圧導体の本数の分類。その構成は、相分離と三相一括とに分類される。 | Angivelse av antall faseledere som finnes inne i samme kapsling (enten en eller tre). | Identyfikacja liczby przewodów WN umieszczonych w jednej obudowie pola wyłącznikowego. Element pola wyłącznikowego może być umieszczony w obudowie jednofazowej lub trójfazowej. | Numero de identificación de los conductores de alta tensión situado en la envolvente de la barra. La barra puede ser también de envolvente unipolar o trifásica. | Identifikacija VN vodiča smještenih u sabirničko kučište. Sabirničko kučište može biti jedno-fazno ili tro-fazno oklopljeno. | Identification of HV conductors number placed in one busbar enclosure. The busbar component can be either 1 phase enclosed or 3 phase enclosed. | Identificarea numarului de conductoare de IT plasate intr-o carcasa de bare. Componenta bara poate fi anvelopata monofazat sau trifazat. | X
| Type of CB-bay enclosure |  | Type of CB-bay enclosure | Typ zapouzdreni vypinacovych poli | Type of CB-bay enclosure | Type d'enveloppe de travée disjoncteur | Art der Leistungsschalterfeldkapselung | ＣＢ回線の圧力容器の分類 | Avgangskapsling | Rodzaj obudowy pola wyłącznikowego | Tipo de envolvente de la posición de interruptor | Tip prekidačkog kučišta | Type of CB-bay enclosure | Tipul carcasei de celula cu intreruptor | X
| Identification of HV conductors number placed in one CB-bay enclosure (except the busbar part of the bay). The CB-bay component can be either single phase enclosed or three phase enclosed. |  | Identification of HV conductors number placed in one CB-bay enclosure (except the busbar part of the bay). The CB-bay component can be either single phase enclosed or three phase enclosed. | Identifikace poctu vodicu vvn nebo zvn umistenych v jednom pouzdre soucasti vypinacovych poli. Vypinacova pole mohou byt bud 1-polove nebo 3-polove zapouzdrene. | Identification of HV conductors number placed in one CB-bay enclosure (except the busbar part of the bay). The CB-bay component can be either single phase enclosed or three phase enclosed. | Nombre de conducteurs HT placés dans une enveloppe de la travée disjoncteur (sauf pour la partie jeu de barres de la travée). Les composants peuvent être ou monophasés ou triphasés | Identifikation der in den Leistungsschalterfeldgehäusen befindlichen Hochspannungsleiter (ohne die dem Feld zugehörigen Teile der Sammelschiene). Die Leistungsschalterfeldkomponente kann entweder einphasig oder dreiphasig gekapselt sein. | １つのＣＢ回線の圧力容器内の高電圧導体の本数の分類（その回線の母線部分は除く）。その構成は、相分離と三相一括とに分類される。 | Angivelse av antall faseledere som finnes inne i samme kapsling, unntatt for samleskinnedelen av avgangen (enten en eller tre). | Identyfikacja liczby przewodów WN umieszczonych w jednej obudowie pola wyłącznikowego. (Za wyjątkiem części szyn pola) Element pola wyłącznikowego może być umieszczony w obudowie jednofazowej lub trójfazowej. | Numero de identificación de los conductores de alta tensión situado en la envolvente de la posición de interruptor (excepto la parte de la barra de la posición). La posición de interruptor puede ser también de envolvente unipolar o trifásica. | Identifikacija VN vodiča smještenih u jedno prekidačko kučište. Prekidačko kučište može biti jedno-fazno ili tro-fazno oklopljeno. | Identification of HV conductors number placed in one CB-bay enclosure (except the busbar part of the bay). The CB-bay component can be either single phase enclosed or three phase enclosed. | Identificarea numarului de conductoare de IT plasate intr-o carcasa de celula cu intreruptor (exceptand barele celulei). Componenta celula cu intreruptor poate fi anvelopata mono sau trifazat. | X
X
| Busbar/Busduct |  | Busbar/Busduct | Pripojnice/Propojeni v polich | Busbar/Busduct | Jeux de barres / barre de liaison | Sammelschiene / Verbindungsbaustein | 母線／母線連絡部 | Busbar/Busduct | Szyna zbiorcza / Szynoprzewód | Barra/Conducto | Sabirnice/Metalom oklopljeni vodič | Busbar/Busduct | Bare/ Bare de legatura |  |  |  |  | X
| Busbar |  | Busbar | Pripojnice | Busbar | jeux de barres | Sammelschiene | 母線 | Samleskinne | Szyna zbiorcza | Barra | Sabirnice | Busbar | Bare |  |  |  |  | X
| Busbar (busbar component) is that part of the switchgear which serves for interconnection between CB-bays. Based on single line diagram, in the switchgear there may be one to several main busbars, transfer busbar or a ring busbar. |  | Busbar (busbar component) is that part of the switchgear which serves for interconnection between CB-bays. Based on single line diagram, in the switchgear there may be one to several main busbars, transfer busbar or a ring busbar. | Pripojnice (soucast pripojnic) je ta cast rozvodneho zarizeni, ktera slouzi pro propojeni mezi vypinacovymi poli. V zavislosti na pouzitem jednopolovem schematu zapojeni hlavnich obvodu muze rozvodne zarizeni mit jednu nebo vice hlavnich pripojnic, pomocnou pripojnici nebo okruzni pripojnici. | Busbar (busbar component) is that part of the switchgear which serves for interconnection between CB-bays. Based on single line diagram, in the switchgear there may be one to several main busbars, transfer busbar or a ring busbar. | Le jeu de barres (composant de jeu de barres) est la partie de l'appareillage assurant la liaison entre les travées disjoncteur. Basé sur le schéma électrique HT du poste, il peut y avoir un ou plusieurs barres principales, ex.: jeu de barres de transfert, jeu de barres en anneau. | Sammelschiene (Sammelschienenkomponente) ist der Teil der Anlage, der die Verbindung zwischen den einzelnen CB-bays darstellt. Je nach Schaltungsart kann die Anlage mehrere Sammelschienen, Umgehungsschienen oder Ringschienen aufweisen. | 母線（母線構成部品）は、ＣＢ回線間を接続するための開閉装置部品。単線結線図では、１つもしくは複数の主母線、補助母線（バイパス断路器での回路切換えなどで使用される主母線名称）、環状母線が開閉装置で適用される。 | Samleskinne (komponenten) er lederen som forbinder effektbryterfeltene. | Szyna zbiorcze (element szyny zbiorczej) jest tą częścią rozdzielniczy, która służy do wzajemnego połączenia między polami wyłącznikowymi. Biorąc pod uwagę schematy jednokreskowe, w rozdzielnicy może znajdować się jedna lub kilka głównych szyn zbiorczych, szyna obejściowa, lub szyny pierścieniowe. | Barra (componente barra) es la parte de la aparamenta que sirve de interconexión entre las posiciones de interruptor. Basandonos en un diagrama unifilar, en la aparamenta pueden haber de una a varias barras principales, barras de transferencia, o una barra en anillo. | Sabirnice (sabirničko kučište) je dio postrojenja koje služi za spajanje između prekidačkih polja. U postrojenju može biti jedna ili više glavnih sabirnica, pomoćne sabirnice itd.. | Busbar (busbar component) is that part of the switchgear which serves for interconnection between CB-bays. Based on single line diagram, in the switchgear there may be one to several main busbars, transfer busbar or a ring busbar. | Barele constituie partea aparatajului de IT asigurand legatura intre celulele cu intreruptor. Functie de schema electrica a statiei de IT, pot fi una sau mai multe bare principale, bare de transfer, bare in inel. |  |  |  |  | X
| Busduct |  | Busduct | Propojeni v polich | Busduct | Barre de liaison | Verbindungsbaustein | 母線連絡部 | Lederseksjon | Szynoprzewód | Conducto | Metalom oklopljeni vodič | Busduct | Bare de legatura |  |  |  |  | X
| Busduct (busduct component) is that part of the switchgear which serves for interconnection of individual apparatus and for connection to outer interface (overhead line bushings, cable boxes, transformer bushings, etc.) within one CB-bay. |  | Busduct (busduct component) is that part of the switchgear which serves for interconnection of individual apparatus and for connection to outer interface (overhead line bushings, cable boxes, transformer bushings, etc.) within one CB-bay. | Propojeni v poli (soucast propojeni v poli) je ta cast rozvodneho zarizeni, ktera slouzi v jednom vypinacovem poli pro propojeni mezi jednotlivymi soucastmi (pristroji) a pro pripojeni na vnejsi interface (pruchodky venkovniho vedeni, kabelove koncovky, pruchodky transformatoru, a pod.) | Busduct (busduct component) is that part of the switchgear which serves for interconnection of individual apparatus and for connection to outer interface (overhead line bushings, cable boxes, transformer bushings, etc.) within one CB-bay. | Barre de liaison, c'est la partie de l'appareillage assurant la liaison entre les différents appareils et le raccordement des interfaces externes (traversée de raccordement aux lignes aériennes, boîtes à câble, traversée de transformateur, etc.…) dans une travée disjoncteur. | Verbindungsbausteine sind die Teile der Anlage, die innerhalb eines Feldes die Verbindung zwischen den einzelner Geräten sowie deren Verbindung zu den äußeren Durchführungen (Freileitungs-, Kabel-, Transformatoranschlüsse, etc.) darstellen. | 母線連絡部 (母線連絡部部品) は、１ＣＢ回線内の各機器間の相互連結及び外部機器（送電線路用ブッシング、ケーブルヘッドや変圧器取合い部ブッシングなど）を接続するための開閉装置部品。 | Lederforbindelse mellom de enkelte komponentene / delene i et felt | Szynoprzewód (element szynoprzewodu) jest tą częścią rozdzielnicy, która służy do wzajemnego połączenia idywidualnych aparatów lub do połączenia z zewnętrznym przyłączem (przepustami do linii napowietrznej, głowicami kablowymi, przepustami transformatora itp.) w jednym polu wyłącznikowym. | Conducto (componente conducto) es la parte de la aparamenta que sirve de interconexión entre los aparatos individuales y la conexión de otros interfaces (bornas de líneas aéreas, botellas terminales, bornas de transformadores, etc...) con la posición de interruptor. | Metalom oklopljeni vodič je dio postrojenja koji služi za povezivanje pojedinačnih aparata i za povezivanje s vanjskim međuspojevima (provodni izolator na nadzemni vod, kabelska kučišta, provodni izolator na transformator itd.) unutar jednog prekidačkog polja. | Busduct (busduct component) is that part of the switchgear which serves for interconnection of individual apparatus and for connection to outer interface (overhead line bushings, cable boxes, transformer bushings, etc.) within one CB-bay. | Barele de legatura constituie partea aparatajului care asigura legatura intre diferite aparate si racordul la interfetele externe (traverse de racord la LEA, cutii de cabluri, borne de transformator etc.) intr-o celula cu intreruptor. |  |  |  |  | X
X
3,1 | Disconnector | 3.1 | Disconnector | Odpojovac | Disconnector | Sectionneur | Trennschalter | 断路器 | Skillebryter | Odłącznik | Seccionador | Rastavljač | Disconnector | Separator |  | X
| IEC 60050 |  | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60 050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 |  | X
| IEV 441-14-05 |  | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 | IEV 441-14-05 |  | X
| A mechanical switching device which provides, in the open position, an isolating distance in accordance with specified requirements. |  | A mechanical switching device which provides, in the open position, an isolating distance in accordance with specified requirements. | Mechanicke spinaci zarizeni, ktere ve vypnute poloze poskytuje izolacni vzdalenost v souladu se specifikovanymi pozadavky | A mechanical switching device which provides, in the open position, an isolating distance in accordance with specified requirements. | Dispositif mécanique de commutation, qui assure en position ouvert une distance d'isolement de sécurité suivant les conditions définies dans la norme CEI correspondante. | Ein mechanisches Schaltgerät, dass in geöffneter Stellung einen Isolationsabstand nach spezifizierten Anforderungen bietet. | 仕様で要求される絶縁距離を開極状態で供給する機械的開閉装置。. | En mekanisk bryter som i åpen stilling har en isolasjonsavstand som oppfyller kravene gitt i spesifikasjoner. | Mechaniczne urządzenie łączeniowe, które zapewnia w pozycji otwartej przerwę izolacyjna zgodną z określonymi wymaganiami. | Dispositivo mecánico de conexión que asegura, en posición abierto, una distancia de aislamiento de acuerdo con las condicciones especificadas. | Mehanički sklopni aparat koji u otvorenom položaju osigurava rastavni razmak u skladu sa specifičnim zahtjevima. | A mechanical switching device which provides, in the open position, an isolating distance in accordance with specified requirements. | Echipament de comutatie mecanic, care asigura, in pozitie deschis o distanta de izolatie in conformitate cu cerintele specificate. |  | X
3.2 | Earthing Switch | 3.2 | Earthing Switch | Uzemnovac | Earthing Switch | Sectionneur de MALT | Erdungsschalter | 接地開閉器 | Jordslutter | Uziemnik | Seccionador de puesta a tierra | Zemljospojnik | Earthing Switch | Cutit de legare la pamant (CLP) |  | X
| IEC 60050 |  | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60 050 | IEC 60050 | IEC 60050 | IEC 60050 | IEC 60050 |  | X
| IEV 441-14-11 |  | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 | IEV 441-14-11 |  | X
| A mechanical switching device for earthing parts of a circuit, capable of withstanding for a specified time currents under abnormal conditions such as those of a short-circuit, but not required to carry current under normal conditions of the circuit. |  | A mechanical switching device for earthing parts of a circuit, capable of withstanding for a specified time currents under abnormal conditions such as those of a short-circuit, but not required to carry current under normal conditions of the circuit. | Mechanicke spinaci zarizeni slouzici k uzemneni casti obvodu, ktere je schopno vydrzet po urcitou dobu prenos proudu za specifikovanych nenormalnich provoznich podminek site jako jsou zkraty, avsak, ktere neni urceno k prenosu proudu za normalnich provoznich podminek site | A mechanical switching device for earthing parts of a circuit, capable of withstanding for a specified time currents under abnormal conditions such as those of a short-circuit, but not required to carry current under normal conditions of the circuit. | Dispositif mécanique de commutation pour mettre à la terre les pièces d'un circuit, capables de supporter le courant de court circuit pour une durée limité 1 ou 3 s, mais non conçu pour transiter le courant nominal du poste. | Ein mechanisches Schaltgerät zum erden eines Stromkreises. Dabei trägt es für einen spezifizierten Zeitraum Ströme unter anormalen Betriebsbedingungen wie Kurzschlüsse. Das Gerät ist jedoch nicht für das Führen von normalen Betriebsströmen vorgesehen. | 回路の接地を取るための機械的開閉装置。接地開閉器は、通常運転時の定格電流通電責務はないが、短絡回路のような事故時に発生する仕様範囲内の短時間電流を通電する能力が必要とされる。 | En mekanisk bryter for å forbinde deler av en krets med jord. Skal kunne føre spesifiserte strømstyrker en spesifisert tid under feil, eksempelvis ved kortslutninger, men trenger ikke å kunne føre strøm under normal drift av anlegget. | Mechaniczne urządzenie łączeniowe do uziemiania części obwodu, zdolne do wytrzymywania w określonym czasie prądów w nienormalnych warunkach, takich jak prądy zwarciowe, ale nie wymaga przewodzenia prądu w normalnych warunkach tego obwodu | Dispositivo mecánico de conexión utilizado para poner a tierra parte de un circuito, capaz de soportar durante un tiempo especificado corrientes en condiciones anormales, tales como cortocircuitos, pero no previsto para soportar corrientes en condiciones normales del circuito | Mehanički sklopni aparat za uzemljivanje dijelova strujnog kruga, sposoban da određeno vrijeme podnese struju u nenormalnim uvjetima pogona kao što je kratki spoj, ali bez sposobnosti da u normalnim pogonskim uvjetima vodi struju. | A mechanical switching device for earthing parts of a circuit, capable of withstanding for a specified time currents under abnormal conditions such as those of a short-circuit, but not required to carry current under normal conditions of the circuit. | Un echipament de comutatie mecanic pe partile de legare la pamant, capabil sa reziste pentru un timp specificat la curenti in conditii anormale, ca acelea de scurtcircuit, dar care nu este solicitat sa conduca curenti in conditii normale. |  | X
X
3.3 | Combined disconnector / Earthing switch | 3.3 | Combined disconnector / Earthing switch | Kombinovany odpojovac-uzemnovac | Combined disconnector / Earthing switch | Combiné Sectionneur / Sectionneur de MALT | Kombinierter Trenn- Erdungsschalter | 複合型断路器接地開閉器 | Kombinert (3 pos.) | Kombinowany odłącznik - uziemnik | Seccionador con cuchilla/s de puesta a tierra | Kombinacija rastavljač - zemljospojnik | Combined disconnector / Earthing switch | Separator/ CLP combinat |  | X
| Combined disconnector / Earthing switch is multifunctional equipment in which the function depends on a position of one common main contact. |  | Combined disconnector / Earthing switch is multifunctional equipment in which the function depends on a position of one common main contact. | Kombinovany odpojovac-uzemnovac je vicefunkcni pristroj, v nemz jeho funkce zavisi na poloze jednoho spolecneho hlavniho kontaktu | Combined disconnector / Earthing switch is multifunctional equipment in which the function depends on a position of one common main contact. | Le combiné sectionneur / sectionneur de MALT est un équipement multifonctions dans lequel la fonction sectionneur ou MALT dépend de la position d'un contact principal commun. | Kombinierte Trenn- / Erdungsschalter sind multifunktionale Geräte, bei denen die Schaltfunktion von der Stellung des gemeinsamen Hauptkontaktes abhängt. | 複合型断路器接地開閉器は、共通の１つの主接点の位置によって断路器と接地開閉器両者の機能を持つ複合型開閉装置。 | Kombinert skillebryter / jordslutter er en multifunksjonskomponent der funksjonen avhenger av posisjonen til en, felles hovedkontakt. | Kombinowany odłącznik - uziemnik jest wielofunkcyjnym urządzeniem, którego funkcja zależy od położenia jednego wspólnego styku. | Seccionador con cuchilla/s de puesta a tierra es un equipo multifuncional cuya función depende de la posición del contacto principal | Kombinacija rastavljač - zemljospojnik je višefunkcionalni aparat čija funkcija ovisi o poziciji jednog zajedničkog glavnog kontakta. | Combined disconnector / Earthing switch is multifunctional equipment in which the function depends on a position of one common main contact. | Este un echipament multifunctional la care functiunea depinde de pozitia unui contact principal comun. |  | X
| Note: In GIS, if there are disconnector and earthing switch with separated drives and contacts placed in one gas compartment, they are considered as stand alone devices. |  | Note: In GIS, if there are disconnector and earthing switch with separated drives and contacts placed in one gas compartment, they are considered as stand alone devices. | Poznamka : V ZRZ, v nemz odpojovac a uzemnovac jsou umisteny v jednom pouzdre, avsak maji samostatne pohony a kontakty, jsou odpojovac a uzemnovac povazovany za dva samostatne pristroje. | Note: In GIS, if there are disconnector and earthing switch with separated drives and contacts placed in one gas compartment, they are considered as stand alone devices. | Note : Dans un GIS, s'il y a sectionneur et un sectionneur de MALT ayant les commandes séparées même si les contacts sont placés dans un compartiment commun de gaz, ils seront considérés comme deux composants séparés. | Anmerkung: Sind in GIS in einem Gasraum Trenn- und Erdungsschalter mit unabhängigen Antrieben angeordnet, so sind sie als Einzelgeräte zu werten. | 注記：GIS機器の中で、断路器と接地開閉器の操作機構と接点が独立している場合は、１つの圧力容器内に収納されている時でも断路器と接地開閉器は独立した機器とする。 | Note: Dersom skillebryter og jordslutter har separate driftsanordninger anses dette som to komponenter. | Uwaga: W rozdzielnicy GIS, jeżeli odłączniki i uziemniki mają oddzielne napędy i styki umieszczone w jednym przedziale gazowym są one traktowane jako oddzielne aparaty. | Nota: En las GIS, si hay seccionadores y seccionadores de puesta a tierra con mandos separados y contactos situados en un compartimento, son considerados como dispositivos independientes | Napomena: U GIS-u, ukoliko postoje rastavljač i zemljospojnik sa odvojenim pogonima i kontaktima smještenim u istom plinskom kučištu smatraju se zasebnim aparatima. | Note: In GIS, if there are disconnector and earthing switch with separated drives and contacts placed in one gas compartment, they are considered as stand alone devices. | Nota: In GIS, daca exista separator si CLP cu mecanisme si contacte plasate intr-un singur compartiment de gaz, sunt considerate ca un dispozitiv de sine statator. |  | X
| Disconnector types |  | Disconnector types
| Centre break (1/6) Double break (2/6) Knee type (horizontal) (3/6) |  | Centre break (1/6) | Horizontalni (1 par hlavnich kontaktu) (1/6) | Centre break (1/6) | Sectionneur ouverture centrale (1/6) | Drehtrennschalter (1/6) | 水平中心１点切（Centre break）(1/6) | Senter-brudd (1/6) | Poziomo obrotowy (1/6) | Apertura central (Dos columnas) (1/6) | Centralni prekid (1/6) | Centre break (1/6) | Separator cu deschidere centrala (1/6) |  | X
X
X
X
X
X
X
X
X
| Vertical (4/6) Semi-pantograph (5/6) Pantograph (6/6) |  | Vertical (4/6) | Vertikalni (4/6) | Vertical (4/6) | Sectionneur ouverture verticale (4/6) | Hebeltrennschalter (4/6) | 垂直１点切（Vertical） (4/6) | Vertikal (4/6) | Sieczny (4/6) | Vertical (4/6) | Vertikalni (4/6) | Vertical (4/6) | Separator cu deschidere verticala (4/6) |  | X
X
X
X
X
X
X
X
X
3.4 | Failure Modes of DS and ES | 3.4 | Failure Modes of Disconnectors | Nezapnul/nevypnul na povel | Does not open/close on command | Ne se ferme pas sur commande/ Ne s'ouvre pas sur commande | Schließt/öffnet nicht auf Kommando | 閉極／開極不能 | Kobler ikke inn/ut på kommando. | Nie zamyka się po podaniu impulsu sterowniczego | No cierra/abre a la orden | Ne isklapa/uklapa na komandu | Does not open/close on command | Nu deschide/ nu inchide la comanda |  | X
| Mi0 - Minor Failure Modes Mi1 - - overheat Mi2 - - misalignment Mi3 - - loss of initial settings Mi4 - - Other Ma0 - Major Failure Modes Ma1 - - Does not close/open on command Ma2 - - Closes/Opens without command Ma3 - - Fails to carry current Ma4 - - Breakdown to earth Ma5 - - Locking in open/closed position Ma6 - - Loss of mechanical integrity Ma7 - - Other |  | Mi0 - Minor Failure Modes Mi1 - - overheat Mi2 - - missalingment Mi3 - - loss of initial settings Mi4 - - Other Ma0 - Major Failure Modes Ma1 - - Does not close/open on comand Ma2 - - Closes/Opens without command Ma3 - - Fails to carry current Ma4 - - Breakdown to earth Ma5 - - Locked in open/closed position Ma6 - - Loss of mechanical integrity Ma7 - - Other | Tento druh poruchy vypovida o elektrickem ovladani nebo o mechanicke funkci odpojovace/uzemnovace | This kind of failure refers to the electrical control and/or mechanical operation of the disconnector / earthing switch. | Ce genre de défaillance concerne le circuit de commande électrique et/ou le mécanisme de commande du sectionneur / du sectionneur de MALT. | Dieser Fehlertyp bezieht sich auf die elektrische Steuerung und/oder den mechanischen Betrieb des Trenn-/Erdungsschalters | 断路器、接地開閉器の電気的な制御回路や操作機構の故障に関する故障。 | Denne feiltyper viser til feil med utløsermekanismen og/eller kontaktbevegelsen, ikke til feil med vernet et kontrollanlegget på stasjonen. | Ten rodzaj uszkodzenia dotyczy elektrycznego sterowania i / lub mechanicznego działania tego odłącznika / uziemnika | Esta clase de fallo se refiere al control eléctrico y/o a la operación mecánica del seccionador / seccionador de puesta a tierra | Ova vrsta kvara odnosi se na električno upravljanje i/ili mehanički pogon rastavljača/zemljospojnika. | This kind of failure refers to the electrical control and/or mechanical operation of the disconnector / earthing switch. | Acest tip de defectare se refera la actionarea electrica si/sau mecanica a separatorului/CLP. |  | X
| Ma1 - Does not open/close on command | 3.5 | Opens/Closes without command | Vypnul/zapnul bez povelu | Opens/Closes without command | Se ferme sans commande/ s'ouvre sans commande | Schließt/öffnet ohne Kommando | 自然投入／開放 | Kobler inn/ut uten kommandosignal. | Zamyka się bez podania impulsu sterowniczego | Cierra/abre sin orden | Isklapa/Uklapa bez komande. | Opens/Closes without command | Deschide/ inchide la comanda |  | X
| This kind of failure refers to the electrical control and/or operating mechanism of the disconnector / earthing switch (not due to failures of the substation protection or control system functions). |  | This kind of failure refers to the electrical control and/or operating mechanism of the disconnector / earthing switch (not due to failures of the substation protection or control system functions). | Tento druh poruchy vypovida o elektrickem ovladani nebo o mechanicke funkci odpojovace/uzemnovace (nikoliv vsak v dusledku poruchy funkce systemu ochran nebo ridiciho systemu v rozvodne) | This kind of failure refers to the electrical control and/or operating mechanism of the disconnector / earthing switch (not due to failures of the substation protection or control system functions). | Ce genre de défaillance concerne le circuit de commande électrique et/ou le mécanisme de commande du sectionneur / du sectionneur de MALT (mais non, en raison d'une défaillance du système de contrôle commande ou de protection de sous-station fonctionne).. | Dieser Fehlertyp bezieht sich auf die elektrische Steuerung und/oder den mechanischen Betrieb des Trenn-/Erdungsschalters (nicht durch Fehler des Anlagenschutzes oder der Anlagensteuerung) | 断路器、接地開閉器の電気的な制御回路や操作機構の故障に関する故障。（ただし、変電所の保護システムや制御回路の故障は除く。） | Denne feiltyper viser til feil med utløsermekanismen og/eller kontaktbevegelsen, ikke til feil med vernet et kontrollanlegget på stasjonen. | Ten rodzaj uszkodzenia dotyczy elektrycznego sterowania i / lub mechanicznego działania tego odłącznika / uziemnika | Esta clase de fallo se refiere al control eléctrico y/o al mecanismo de accionamiento del seccionador / seccionador de puesta a tierra (no debido a fallos en las funciones de los sistemas de protección o de control) | Ova vrsta kvara odnosi se na električno upravljanje i/ili pogonski mehanizam rastavljača/zemljospojnika (ne na kvar zaštite ili upravljanja postrojenja). | This kind of failure refers to the electrical control and/or operating mechanism of the disconnector / earthing switch (not due to failures of the substation protection or control system functions). | Acest tip de defectare se refera la mecanismul electric de control si/sau de actionare al separatorului/CLP (nu se datoreaza defectarilor functiilor de protectie ale statiei sau sistemului de control). |  | X
| Ma2 - Opens/Closes without command | 3.5 | Opens/Closes without command | Vypnul/zapnul bez povelu | Opens/Closes without command | Se ferme sans commande/ s'ouvre sans commande | Schließt/öffnet ohne Kommando | 自然投入／開放 | Kobler inn/ut uten kommandosignal. | Zamyka się bez podania impulsu sterowniczego | Cierra/abre sin orden | Isklapa/Uklapa bez komande. | Opens/Closes without command | Deschide/ inchide la comanda |  | X
| This kind of failure refers to the electrical control and/or operating mechanism of the disconnector / earthing switch (not due to failures of the substation protection or control system functions). |  | This kind of failure refers to the electrical control and/or operating mechanism of the disconnector / earthing switch (not due to failures of the substation protection or control system functions). | Tento druh poruchy vypovida o elektrickem ovladani nebo o mechanicke funkci odpojovace/uzemnovace (nikoliv vsak v dusledku poruchy funkce systemu ochran nebo ridiciho systemu v rozvodne) | This kind of failure refers to the electrical control and/or operating mechanism of the disconnector / earthing switch (not due to failures of the substation protection or control system functions). | Ce genre de défaillance concerne le circuit de commande électrique et/ou le mécanisme de commande du sectionneur / du sectionneur de MALT (mais non, en raison d'une défaillance du système de contrôle commande ou de protection de sous-station fonctionne).. | Dieser Fehlertyp bezieht sich auf die elektrische Steuerung und/oder den mechanischen Betrieb des Trenn-/Erdungsschalters (nicht durch Fehler des Anlagenschutzes oder der Anlagensteuerung) | 断路器、接地開閉器の電気的な制御回路や操作機構の故障に関する故障。（ただし、変電所の保護システムや制御回路の故障は除く。） | Denne feiltyper viser til feil med utløsermekanismen og/eller kontaktbevegelsen, ikke til feil med vernet et kontrollanlegget på stasjonen. | Ten rodzaj uszkodzenia dotyczy elektrycznego sterowania i / lub mechanicznego działania tego odłącznika / uziemnika | Esta clase de fallo se refiere al control eléctrico y/o al mecanismo de accionamiento del seccionador / seccionador de puesta a tierra (no debido a fallos en las funciones de los sistemas de protección o de control) | Ova vrsta kvara odnosi se na električno upravljanje i/ili pogonski mehanizam rastavljača/zemljospojnika (ne na kvar zaštite ili upravljanja postrojenja). | This kind of failure refers to the electrical control and/or operating mechanism of the disconnector / earthing switch (not due to failures of the substation protection or control system functions). | Acest tip de defectare se refera la mecanismul electric de control si/sau de actionare al separatorului/CLP (nu se datoreaza defectarilor functiilor de protectie ale statiei sau sistemului de control). |  | X
| Ma3 - Fails to carry current | 3.6 | Fails to carry current | Neprenesl proud | Fails to carry current | Ne transite pas le courant | Trägt den Strom nicht | 通電異常 | Greier ikke å føre strøm i innkoblet posisjon. | Nie przewodzi prądu | No conduce corriente | Ne vodi struju | Fails to carry current | Nu conduce curentul |  | X
| This kind of failure refers to an electrical phenomena in the contact system of the disconnector / earthing switch at the closing position. |  | This kind of failure refers to an electrical phenomena in the contact system of the disconnector / earthing switch at the closing position. | Tento druh poruchy vypovida o elektrickem jevu v kontaktnim systemu nebo na primarnim pripojeni odpojovace/uzemnovace v zapnutem stavu. | This kind of failure refers to an electrical phenomena in the contact system of the disconnector / earthing switch at the closing position. | Cette défaillance concerne les contacts électriques du sectionneur / du sectionneur de MALT en position fermée. | Dieser Fehlertyp bezieht sich auf einen elektrischen Effekt im Kontaktsystem oder den Primäranschlüssen eines Trenn-/Erdungsschalters im eingeschalteten Zustand. | 断路器、接地開閉器が投入状態の時の故障であり、接点部品の電気的特性変化に起因する。 | Denne feiltypen viser til elektriske fenomener (varmgang etc.) i kontaktsystemet skillebryteren / jordslutteren mens den er innkoblet. | Ten rodzaj uszkodzenia dotyczy elektrycznych zjawisk systemu stykowego odłącznika / uziemnika | Esta clase de fallo se refiere a un fenómeno eléctrico en los contactos del seccionador / seccionador de p.a.t. en la posición de cerrado | Ova vrsta kvara odnosi se na električke pojave u kontaktnom sistemu rastavljača / zemljospojnika u uklopljenom položaju. | This kind of failure refers to an electrical phenomena in the contact system of the disconnector / earthing switch at the closing position. | Acest tip de defectare se refera la un fenomen electric in sistemul de contact al separatorului/CLP in pozitie inchisa. |  | X
| Ma4 - Breakdown to earth | 3.7 | Breakdown to earth | Zkrat | Breakdown to earth | Défaut à la terre | Durchschlag zur Erde | 対地閃絡 | Overslag til jord | Przebicie izolacji doziemnej | Defecto a tierra | Proboj prema zemlji | Breakdown to earth | Scurtcircuit la pamant |  | X
| This kind of failure refers to a electrical breakdown between parts of the disconnector / earthing switch at service voltage and earthed parts in the substation. |  | This kind of failure refers to a electrical breakdown between parts of the disconnector / earthing switch at service voltage and earthed parts in the substation. | Tento druh poruchy vypovida o elektrickem preskoku mezi castmi odpojovace/uzemnovace pod napetim vvn nebo zvn a uzemnenymi castmi nebo zemi | This kind of failure refers to a electrical breakdown between parts of the disconnector / earthing switch at service voltage and earthed parts in the substation. | Cette défaillance se caractérise par franchissement de l'isolement entre les parties du sectionneur / sectionneur de MALT sous tension de service et les pièces reliées à la terre | Dieser Fehlertyp bezieht sich auf einen elektrischen Durchschlag zwischen Teilen des Trenn-/Erdungsschalters auf Hochspannungspotential und geerdeten Teilen. | 課電状態の断路器、接地開閉器の部品と対地間で発生した電気的絶縁破壊。 | Denne feiltypen viser til overslag / gjennomslag mellom deler av bryteren som er på høyspenningspotensial og jordede deler. | Ten rodzaj uszkodzenia dotyczy elektrycznego przebicia izolacji pomiędzy częściami odłącznika / uziemnika na napięciu roboczym, a częściami uziemionymi w stacji. | Esta clase de fallo se refiere a una falta entre partes del seccionador / seccionador de p.a.t. a la tensión de servicio y partes puestas a tierra en la subestación | Ova vrsta kvara odnosi se na električki proboj između dijelova rastavljača / zemljospojnika na pogonskom naponu i uzemljenih dijelova u postrojenju | This kind of failure refers to a electrical breakdown between parts of the disconnector / earthing switch at service voltage and earthed parts in the substation. | Acest tip de defectare se refera la scurtcircuitul intre partile separatorului/CLP la tensiunea de serviciu si partile la pamant ale statiei. |  | X
| Ma5 - Locking in open or closed position | 3.11 | Locking in open or closed position | Zablokovani ve vypnute nebo zapnute poloze | Locking in open or closed position | Blocage en position Ouvert ou Fermée | Gesperrt in AUS oder EIN Schaltstellung | 開極、閉極状態での鎖錠。 | Låst i utkoblet eller innkoblet stilling. | Zablokowanie w pozycji otwartej lub zamkniętej | Bloqueo en posición abierto o cerrado | Blokira u isklopljenom ili uklopljenom položaju | Locking in open or closed position | Blocare (zavorare in pozitie inchisa sau deschisa) |  | X
| (alarm has been triggered by the control system) This kind of failure refers to an electrical blocking set by the control system of the disconnector / earthing switch. This failure characteristic is not meant for situations where the locking is discovered while giving a command to open or to close. In that case the failure mode “Does not close or open on command” is applicable. |  | This kind of failure refers to an electrical blocking set by the control system of the disconnector / earthing switch. This failure characteristic is not meant for situations where the locking is discovered while giving a command to open or to close. In that case the failure mode “Does not close or open on command” is applicable. | Tento druh poruchy vypovida o elektrickem zablokovani funkce vlastnim blokovacim systemem odpojovace/uzemnovace. Tento druh poruchy se netyka situace, pri niz je zablokovani objeveno az v okamziku vyslani povelu ZAP nebo VYP (porucha typu "nezypnul/nevypnul na povel"). | This kind of failure refers to an electrical blocking set by the control system of the disconnector / earthing switch. This failure characteristic is not meant for situations where the locking is discovered while giving a command to open or to close. In that case the failure mode “Does not close or open on command” is applicable. | Cette défaillance se caractérise par un blocage électrique du système de contrôle commande du sectionneur / sectionneur de MALT. Cette défaillance n'est pas signifiée quand le blocage est découvert lors d'une commande d'ouverture ou d'ouverture. Dans ce cas le mode de défaillance "ne se ferme pas ou ne s'ouvre pas" est applicable. | Dieser Fehlertyp bezieht sich auf eine elektrische Sperre, die durch die Steuerung des Trenn-/Erdungsschalters gesetzt wurde. Diese Fehlerart trifft nicht für Fälle zu, bei denen die Sperre erst während der Kommandogabe für eine EIN- oder AUS-Schaltung bemerkt wird. In diesen Fällen ist der Fehlertyp "Schließt nicht auf Kommando; öffnet nicht auf Kommando" zu wählen. | 断路器、接地開閉器の制御システムの電気的鎖錠装置に関する故障。その故障の特徴は、鎖錠が発見された部位や開閉極指令を与える状態とは無関係であることである。その場合の故障モードは、”開閉極不能”が適用される。 | Denne feiltypen angir når bryterens utløsermekanisme har "låst seg". Denne feiltypen er ikke ment å omfatte situasjoner når blokkeringen er oppdaget i forbindelse med koblinger. I såfall er feiltypen "Kobler ikke på kommando". | Ten rodzaj uszkoodzenia dotyczy elektrycznego blokowania spowodowanego przez układ sterowania odłącznika / uziemnika. Ta cecha uszkodzenia nie ma znaczenia w sytuacji, w której blokada została stwierdzona po podaniu impulsu na otwarcie lub zamknięcie. W takim przypadku ma zastosowanie tryb uszkodzenia "Nie zamyka się lub nie otwiera się po podaniu impulsu sterowniczego". | Esta clase de fallo se refiere a un bloqueo eléctrico establecido por el sistema de control del seccionador / seccionador de p.a.t. Este fallo característico no es aplicable a situaciones, donde el bloqueo es descubierto mientras se da una orden de apertura o cierre. En ese caso, el tipo de fallo es "No abre o no cierra a la orden" | Ova vrsta kvara odnosi se na električne blokade i kontrolu rastavljača / zemljospojnika. Ne radi se o kvaru koji je uočen za vrijeme sklopnih operacija. Tada se primjenjuje kvar "ne uklapa/isklapa na komandu". | This kind of failure refers to an electrical blocking set by the control system of the disconnector / earthing switch. This failure characteristic is not meant for situations where the locking is discovered while giving a command to open or to close. In that case the failure mode “Does not close or open on command” is applicable. | Acest tip de defectare se refera la o blocare electrica data de sistemul de control al separatorului/CLP. Aceasta defectare nu se refera la situatiile cand blocarea (zavorirea) este descoperita in timpul unei comenzi de inchidere sau deschidere. In acest caz este aplicabil modul de defectare "Nu inchide sau nu deschide la comanda". |  | X
Ma6 - Loss of mechanical integrity
| Ma7 - others | 3.11 | Locking in open or closed position | Zablokovani ve vypnute nebo zapnute poloze | Locking in open or closed position | Blocage en position Ouvert ou Fermée | Gesperrt in AUS oder EIN Schaltstellung | 開極、閉極状態での鎖錠。 | Låst i utkoblet eller innkoblet stilling. | Zablokowanie w pozycji otwartej lub zamkniętej | Bloqueo en posición abierto o cerrado | Blokira u isklopljenom ili uklopljenom položaju | Locking in open or closed position | Blocare (zavorare in pozitie inchisa sau deschisa) |  | X
| * Breakdown between poles - This kind of failure refers to a electrical breakdown between parts at service voltage of different poles of the disconnector / earthing switch. * Breakdown across pole during operation * Does not make/break the current - This kind of failure refers to a electrical phenomena in the contact system of the disconnector / earthing switch during closing and opening operations. * Breakdown across pole in open position - This kind of failure refers to a electrical breakdown between the contacts or the terminals of the disconnector / earthing switch within one pole. |  | This kind of failure refers to an electrical blocking set by the control system of the disconnector / earthing switch. This failure characteristic is not meant for situations where the locking is discovered while giving a command to open or to close. In that case the failure mode “Does not close or open on command” is applicable. | Tento druh poruchy vypovida o elektrickem zablokovani funkce vlastnim blokovacim systemem odpojovace/uzemnovace. Tento druh poruchy se netyka situace, pri niz je zablokovani objeveno az v okamziku vyslani povelu ZAP nebo VYP (porucha typu "nezypnul/nevypnul na povel"). | This kind of failure refers to an electrical blocking set by the control system of the disconnector / earthing switch. This failure characteristic is not meant for situations where the locking is discovered while giving a command to open or to close. In that case the failure mode “Does not close or open on command” is applicable. | Cette défaillance se caractérise par un blocage électrique du système de contrôle commande du sectionneur / sectionneur de MALT. Cette défaillance n'est pas signifiée quand le blocage est découvert lors d'une commande d'ouverture ou d'ouverture. Dans ce cas le mode de défaillance "ne se ferme pas ou ne s'ouvre pas" est applicable. | Dieser Fehlertyp bezieht sich auf eine elektrische Sperre, die durch die Steuerung des Trenn-/Erdungsschalters gesetzt wurde. Diese Fehlerart trifft nicht für Fälle zu, bei denen die Sperre erst während der Kommandogabe für eine EIN- oder AUS-Schaltung bemerkt wird. In diesen Fällen ist der Fehlertyp "Schließt nicht auf Kommando; öffnet nicht auf Kommando" zu wählen. | 断路器、接地開閉器の制御システムの電気的鎖錠装置に関する故障。その故障の特徴は、鎖錠が発見された部位や開閉極指令を与える状態とは無関係であることである。その場合の故障モードは、”開閉極不能”が適用される。 | Denne feiltypen angir når bryterens utløsermekanisme har "låst seg". Denne feiltypen er ikke ment å omfatte situasjoner når blokkeringen er oppdaget i forbindelse med koblinger. I såfall er feiltypen "Kobler ikke på kommando". | Ten rodzaj uszkoodzenia dotyczy elektrycznego blokowania spowodowanego przez układ sterowania odłącznika / uziemnika. Ta cecha uszkodzenia nie ma znaczenia w sytuacji, w której blokada została stwierdzona po podaniu impulsu na otwarcie lub zamknięcie. W takim przypadku ma zastosowanie tryb uszkodzenia "Nie zamyka się lub nie otwiera się po podaniu impulsu sterowniczego". | Esta clase de fallo se refiere a un bloqueo eléctrico establecido por el sistema de control del seccionador / seccionador de p.a.t. Este fallo característico no es aplicable a situaciones, donde el bloqueo es descubierto mientras se da una orden de apertura o cierre. En ese caso, el tipo de fallo es "No abre o no cierra a la orden" | Ova vrsta kvara odnosi se na električne blokade i kontrolu rastavljača / zemljospojnika. Ne radi se o kvaru koji je uočen za vrijeme sklopnih operacija. Tada se primjenjuje kvar "ne uklapa/isklapa na komandu". | This kind of failure refers to an electrical blocking set by the control system of the disconnector / earthing switch. This failure characteristic is not meant for situations where the locking is discovered while giving a command to open or to close. In that case the failure mode “Does not close or open on command” is applicable. | Acest tip de defectare se refera la o blocare electrica data de sistemul de control al separatorului/CLP. Aceasta defectare nu se refera la situatiile cand blocarea (zavorirea) este descoperita in timpul unei comenzi de inchidere sau deschidere. In acest caz este aplicabil modul de defectare "Nu inchide sau nu deschide la comanda". |  | X
X
| CT primary arrangement – Hair pin or eyebolt types (1/4) |  | CT primary arrangement – Hair pin or eyebolt types (1/4) | Usporadani primarni casti PTP - "sponka" nebo "usni lalucek" | CT primary arrangement – Hair pin or eyebolt types (1/4) | Tc primaire – En épingle à cheveux ou en oeillet(1/4) | CT Primäranordnung - Haarnadel-Bauweise oder Nadelöhrbauweise (1/4) | 計器用変成器の主要構造 – ヘアピン形やアイボルト形（Hair pin or eyebolt types） (1/4) | Strømtranformatorens primærkrets arrangement – "Hårnål" eller "øyebolt" type (1/4) | Układ uzwojenia pierwotnego przekładnika prądowego (hair pin or eyebolt) | Devanado primario del TI – Horquilla o perno de argolla (1/4) (Hair pin or eyebolt types) | Izvedba primara strujnog transformatora - osigurač ili bolcna (1/4) | CT primary arrangement – Hair pin or eyebolt types (1/4) | Primarul TC - in ac de par (spelca, bolt) (1/4) |  |  | X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
| CT primary arrangement – Bar primary or top core (2/4) |  | CT primary arrangement – Bar primary or top core (2/4) | Usporadani primarni casti PTP – primy primarni vodic | CT primary arrangement – Bar primary or top core (2/4) | Tc primaire - barre primaire traversante ou primaire sous tension (2/4) | CT Primäranordnung - Massiver Primärleiter oder Kopfstromwandler (2/4) | 計器用変成器の主要構造 – Bar primary or top core (2/4) | Strømtranformatorens primærkrets arrangement – "Stav" eller "toppkjerne" (2/4) | Układ uzwojenia pierwotnego przekładnika prądowego (hair pin or eyebolt) | Devanado primario del TI – Primario en barra o pirmario en cabeza (invertido) (2/4) | Izvedba primara strujnog transformatora - štapni primar ili top core (2/4) | CT primary arrangement – Bar primary or top core (2/4) | Primarul TC - bara primara traversanta sau primar sub tensiune (2/4) |  |  | X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
| CT primary arrangement – Cascade type (3/4) |  | CT primary arrangement – Cascade type (3/4) | Usporadani primarni casti PTP – kaskadni typ | CT primary arrangement – Cascade type (3/4) | Tc primaire - enroulement en cascade(3/4) | CT Primäranordnung - Kaskadenbauweise (3/4) | 計器用変成器の主要構造 – カスケード形 (3/4) | Strømtranformatorens primærkrets arrangement – "Kaskade" (3/4) | Układ uzwojenia pierwotnego przekładnika prądowego - typu kaskadowego | Devanado primario del TI – Tipo cascada (3/4) | Izvedba primara strujnog transformatora - kaskada (3/4) | CT primary arrangement – Cascade type (3/4) | Primarul TC - in cascada (3/4) |  |  | X
X
X
X
X
X
X
X
X
X
X
X
X
X
X
| IT primary diagnostic tests |  | IT primary diagnostic tests | Diagnosticka zkouska primarni casti PT | IT primary diagnostic tests | Transformateur de mesure tests de diagnostique circuit primaire | Diagnoseprüfungen des Wandlerprimärteils | 計器用変成器の一次側診断 | Diagnostisk test på primærsiden av måletransformatoren | Pomiary diagnostyczne uzwojenia pierwotnego przekładnika | Medidas de diagnostico del primario del TM | Dijagnostički test primara mjernog transformatora | IT primary diagnostic tests | Teste primare de diagnosticare la transformatoarele de masura |  |  | X
| IT primary diagnostic tests include all tests that are performed on HV site of complete IT installation, e.g. power factor measurement, capacitance measurement, insulation resistance measurement, primary resistance measurements, PD measurements . |  | IT primary diagnostic tests include all tests that are performed on HV site of complete IT installation, e.g. power factor measurement, capacitance measurement, insulation resistance measurement, primary resistance measurements, PD measurements . | Diagnosticka zkouska primarni casti PT zahrnuje vsechny zkousky provadene na primarni strane vvn nebo zvn kompletni instalace PT, napr. mereni ztratoveho cinitele, mereni kapacit, mereni izolacniho odporu, mereni odporu primarniho vinuti, mereni castecnych vyboju. | IT primary diagnostic tests include all tests that are performed on HV site of complete IT installation, e.g. power factor measurement, capacitance measurement, insulation resistance measurement, primary resistance measurements, PD measurements . | Les tests de diagnostique primaires incluent tous les essais qui sont réalisés sur site de l'ensemble du transformateur de mesure, mesure du facteur de puissance, mesure de la capacité, mesure de la résistance d'isolation, mesures de la résistance du primaire, mesures de DP. | Diagnoseprüfungen des Wandlerprimärteils beinhalten alle Prüfungen, die auf der Hochspannungsseite der Wandleranordnung durchgeführt werden (z.B. Leistungsfaktormessung, Kapazitätsmessung, Messung des Isolationswiderstandes, Widerstandsmessung des Primärpfades, Teilentladungsmessung). | 据付け後の計器用変成器について、高圧側で実施される全ての試験。（例：tanδ測定、静電容量測定、絶縁抵抗測定、一次巻線抵抗測定、部分放電測定）。 | Primærside diagnose omfatter alle tester som gjennomføres på høyspenningssiden, eksempelsvis tapsmålinger, kapasitansmålinger, isolasjonsmotstand, utladningsmålinger etc. | Pomiary diagnostyczne strony pierwotnej przekładników obejmują wszystkie pomiary, które wykonywane po stronie WN kompletnego przekładnika np. pomiar współczynnika mocy, pomiary pojemności, pomiary rezystancji izolacji, pomiary rezystancji uzwojenia pierwotnego, pomiary wyładowań niezupełnych. | Medidas de diagnostico del primario del TM incluyen todos los ensayos que se realizan en la parte de AT de un transformador de medida, p.e. medidas de factor de potencia, medida de capacidad, medida de resistencia de aislamiento, medida de resistencia del primario, medidas de descargas parciales. | Dijagnostička ispitivanja primara mjernog transformatora uključuju sva ispitivanja koja se provode na VN strani kompletne instalacije transformatora, npr. mjerenje faktora snage, kapaciteta, otpora izolacije, otpora primara, parcijalna izbijanja. | IT primary diagnostic tests include all tests that are performed on HV site of complete IT installation, e.g. power factor measurement, capacitance measurement, insulation resistance measurement, primary resistance measurements, PD measurements . | Testele primare de diagnosticare la transformatoarele de masura include toate testele care se fac pe partea de IT a instalatiei complete de transformator de masura, de ex. masurarea factorului de putere, masurarea capacitatii, masurarea rezistentei de izolare, masurarea rezistentei primare, masuratori de descarcari partiale. |  |  | X
X
| IT secondary diagnostic tests |  | IT secondary diagnostic tests | Diagnosticka zkouska sekundarni casti PT | IT secondary diagnostic tests | Transformateur de mesure tests de diagnostique circuit secondaire | Diagnoseprüfungen des Wandlersekundärteils | 計器用変成器の二次側診断 | Diagnostisk test på sekundærsiden av måletransformatoren | Pomiary diagnostyczne uzwojenia wtórnego przekładnika | Medidas de diagnostico del secundario del TM | Dijagnostički test sekundara mjernog transformatora | IT secondary diagnostic tests | Teste secundare de diagnosticare la transformatoarele de masura |  |  | X
| IT secondary diagnostic tests include all tests that are performed on secondary site of complete IT installation e.g. calibration (accuracy check), open triangle voltage, insulation resistance measurement, secondary resistance measurements, external cable insulation, monitoring devices operation and accuracy tests, damping circuit components characteristics measurement. |  | IT secondary diagnostic tests include all tests that are performed on secondary site of complete IT installation e.g. calibration (accuracy check), open triangle voltage, insulation resistance measurement, secondary resistance measurements, external cable insulation, monitoring devices operation and accuracy tests, damping circuit components characteristics measurement. | Diagnosticka zkouska sekundarni casti PT zahrnuje vsechny zkousky provadene na sekundarni strane kompletni instalace PT, napr. kalibraci (mereni presnosti), mereni napeti na svorkach vinuti se zapojenim do otevreneho trojuhelnika, mereni izolacniho odporu, mereni odporu sekundarnich vinuti, mereni izolace externich kabelu, mereni funkce a presnosti monitorovacich systemu, mereni charakteristik tlumicich a kompenzacnich obvodu, a pod. | IT secondary diagnostic tests include all tests that are performed on secondary site of complete IT installation e.g. calibration (accuracy check), open triangle voltage, insulation resistance measurement, secondary resistance measurements, external cable insulation, monitoring devices operation and accuracy tests, damping circuit components characteristics measurement. | les tests de diagnostic secondaires incluent tous les essais qui sont réalisés sur site au secondaire du transformateur de mesure. calibrage par exemple (contrôle de la précision), tension triangle delta ouvert, mesure de la résistance d'isolement, mesures de la résistance du secondaires, isolation externe des câbles, dispositif de surveillant, tests de précision, mesure de la caractéristiques d'amortissement. | Diagnoseprüfungen des Wandlersekundärteils beinhalten alle Prüfungen, die auf der Sekundarseite einer Wandleranordnung durchgeführt werden (z.B. Kalibrierung, Messung der offenen Dreieckspannung, Messung des Isolationswiderstandes, Widerstandsmessung des Sekundärkreises, Messung der externen Kabelisolation, Überprüfung der Funktion und Richtigkeit von Monitoring-Geräten, Messung der Charakteristika von Dämpfungskomponenten). | 据付け後の計器用変成器について、低圧側で実施される全ての試験。（例：誤差チェック、残留電圧測定、絶縁抵抗測定、二次巻線抵抗測定、外部接続ケーブルの絶縁監視装置の動作と精度確認、減衰回路要素の特性測定）。 | Sekundærsidediagnose omfatter alle tester som gjennføres på sekundærsiden, eksempelvis kalibrering, isolasjonsmotstand, måling på dempekretser etc.) | Pomiary diagnostyczne strony wtórnej przekładników obejmują wszystkie pomiary, które są wykonwane po stronie wtórnej kompletnego przekładnika np. kalibrację (sprawdzenie dokładności), napięcie otwartego trójkąta, pomiar rezystancji izolacji, pomiary rezystancji uzwojeń wtórnych, izolację kabli zewnętrznych, działanie urządzeń monitorujących i pomiary dokładności, pomiary parametrów elementów obwodu tłumiącego. | Medidas de diagnostico del secundario del TM incluyen todos los ensayos que se realizan en el secundario de un trasnformador de medida, p.e. calibración (control de precisión), tensión a triangulo abierto, medida de resistencia de aislamiento, medida de resistencia del secundario, aislamiento del cable externo, dispositivos de monitorización de operaciones y ensayos de precisión, medidas características de los componentes del compensador | Dijagnostička ispitivanja sekundara mjernog transformatora uključuju sva ispitivanja koja se provode na sekundarnoj strani kompletne instalacije transformatora, npr. kalibriranje (provjera klase), napon otvorenog trokuta, mjerenje otpora izolacije, otpor sekundarnog kruga itd. | IT secondary diagnostic tests include all tests that are performed on secondary site of complete IT installation e.g. calibration (accuracy check), open triangle voltage, insulation resistance measurement, secondary resistance measurements, external cable insulation, monitoring devices operation and accuracy tests, damping circuit components characteristics measurement. | Testele secundare de diagnosticare la trafo masura includ toate testele care se fac pe partea secundara a instalatiei complete de trafo masura, de ex. calibrarea ( verificarea de acuratete), masuratori de tensiune, rezistenta de izolatie, rezistenta secundara, izolatia cablului, functionarea echipamentului de monitorizare si teste de acuratete, masuratorile caracteristicilor componentelor circuitului antiferorezonant. |  |  | X
X
| Sample of insulation medium diagnostic tests |  | Sample of insulation medium diagnostic tests | Diagnosticka zkouska vzorku izolacniho media | Sample of insulation medium diagnostic tests | Échantillon pour tests de diagnostique du milieu isolement. | Diagnosetest an einer Probe des Isoliermaterials | 絶縁媒体のサンプル診断 | Prøvetaking og undersøkelse av isolasjonsmedium | Pomiary diagnostycne próbki medium izolacyjnego | Medidas de diagnostico a muestras del medio aislante | Dijagnostički test uzorka izolacijskog medija | Sample of insulation medium diagnostic tests | Teste de diagnosticare a mediului de izolatie | X |  | X
| Sample of insulation medium diagnostic tests include all tests that are performed on insulation medium sample withdrawn from the IT, e.g. dissolved gas analysis, chemical and electrical analysis of oil, humidity content in SF6, SF6 by-products content in SF6, air content in SF6. |  | Sample of insulation medium diagnostic tests include all tests that are performed on insulation medium sample withdrawn from the IT, e.g. dissolved gas analysis, chemical and electrical analysis of oil, humidity content in SF6, SF6 by-products content in SF6, air content in SF6. | Diagnosticka zkouska vzorku izolacniho media zahrnuje vsechny zkousky provadene na vzorku izolacniho media odebraneho z PT, napr. analyza rozpustenych plynu (DGA), chemicko-fyzikalni analyza oleje, mereni vlhkosti SF6, mereni obsahu rozkladnych produktu SF6, mereni obsahu SF6, a pod. | Sample of insulation medium diagnostic tests include all tests that are performed on insulation medium sample withdrawn from the IT, e.g. dissolved gas analysis, chemical and electrical analysis of oil, humidity content in SF6, SF6 by-products content in SF6, air content in SF6. | Tests de diagnostique sur échantillon du milieu isolant, ils incluent tous les essais qui sont réalisés sur échantillon du milieu isolant prélevé du transformateur de mesure, analyse des gaz dissous, analyse chimique et diélectrique de l'huile, taux d'hygrométrie du SF6, analyse des produits de décomposition du SF6, % d'air dans SF6 etc. | Ein Diagnosetest an einer Probe des Isoliermaterials beinhaltet alle Prüfungen, die an einer aus dem Wandler entnommenen Probe des Isolationsmediums durchgeführt werden (z.B. Analyse von gelösten Gasen, chemische oder elektrische Analyse des Öls, Feuchteanteil in SF6, Anteil von SF6-Zersetzungsprodukten, Luftanteil in SF6). | 計器用変成器から採取される絶縁媒体について実施される全ての試験。（例：溶存ガス分析、絶縁油の科学的、電気的分析、SF6ガス中水分量、SF6中の分解ガス含有量、SF6ガス中の空気の含有量） | Prøvetaking og undersøkelse av isolasjonsmedium omfatter alle tester på en prøve av isolasjonsmediet, eksempelvis analyse av løste gasser, kjemiske analyser, fukt, luftinnhold i SF6 etc. | Pomiary diagnostyczne próbki medium izolacyjnego obejmują wszystkie próby, które są wykonywane na próbce medium izolacyjnego pobranego z przekładnika np. analizę rozpuszczonych gazów, analizy chemiczne i badania elektryczne oleju, zawartość wody w SF6, zawartość produktów rozpadu w SF6, zawartość powietrza w SF6. | Medidas de diagnostico a muestras del medio aislante incluye todos los analisis que se realicen a muestras del medio aislante extraidas del transformador de medida, analisis de gases disueltos, analisis fisico-químicos y electricos al aceite, contenido de humedad del SF6, productos de descomposición del SF6, %SF6. | Dijagnostička ispitivanja uzorka izolacijskog medija uključuju sva ispitivanja koja se provode na izolacijskom mediju izvađenom iz mjernog transformatora, npr. analiza plinova, kemijska i električka analiza ulja, sadržaja vlage u plinu SF6, sadržaja produkata raspada u plinu SF6, sadržaja zraka u plinu SF6. | Sample of insulation medium diagnostic tests include all tests that are performed on insulation medium sample withdrawn from the IT, e.g. dissolved gas analysis, chemical and electrical analysis of oil, humidity content in SF6, SF6 by-products content in SF6, air content in SF6. | Testele de diagnosticare a mediului de izolatie includ toate testele care se fac asupra mediului de izolatie al unui trafo de masura, de ex. analiza gazelor dizolvate, analiza chimica si electrica a uleiului, continutul de umiditate in SF6, continutul de aer in SF6 etc. | X |  | X
[15 empty] | X |  | X
| Retrofit |  | Retrofit | Retrofit | Retrofit | Remise en état générale, modification | Nachrüstung | 装置改造 | Oppgradering (retrofit) | Modernizacja | Modernización | Naknadna ugradnja | Retrofit | Reabilitare (Retrofit) | X | X | X | X | X | X
| Work (activity) to equip a device with new parts or equipment not available previously. |  | Work (activity) to equip a device with new parts or equipment not available previously. | Prace, pri niz je zarizeni vybaveno novymi konstrukcnimi castmi, které puvodne neobsahovalo | Work (activity) to equip a device with new parts or equipment not available previously. | Reprise générale d'un appareil et l'équiper de nouvelles pièces ou de nouveaux composant pour en améliorer la fiabilité. | Arbeit (Aktivität) zur Ausrüstung eines Gerätes mit neuen Teilen oder Einrichtungen, die bislang nicht verfügbar waren. | 適用実績のない機器や新しい部品を持つ装置を装備するための作業。 | Arbeid med å utstyre en komponent med deler som ikke var tilgjengelige tidligere. | Praca (działanie) mające na celu wyposażenie urządzenia w nowe części lub sprzęt nie dostępny poprzednio. | Trabajos para equipar a un dispositivo con nuevas partes o equipos no disponibles previamente. Work (activity) to equip a device with new parts or equipment not available previously. | Aktivnosti za opremanje uređaja s novim dijelom ili opremom koja prije nije bila dostupna. | Work (activity) to equip a device with new parts or equipment not available previously. | Lucrare (activitate) de echipare a unei instalatii cu parti sau echipamente noi, indisponibile anterior. | X | X | X | X | X | X
| Upgrading |  | Upgrading | Zvyseni parametru | Upgrading | Amélioration des performances. | Aufwertung | 品質改善 | Oppgradering | Upgrading | Mejora | Nadogradnja | Upgrading | Retehnologizare (Upgrading) | X | X | X | X | X | X
| Work (activity) to improve the quality of equipment. |  | Work (activity) to improve the quality of equipment. | Prace na zarizeni s cilem zvysit kvalitu (parametry) zarizeni | Work (activity) to improve the quality of equipment. | Activité pour améliorer la qualité de l'équipement. | Arbeit (Aktivität) zur Erhöhung der Qualität eines Gerätes. | 機器の品質工場作業。 | Arbeid med å forbedre egenskapene / kvaliteten til utstyret. | Work (activity) to improve the quality of equipment. | Trabajos para mejorar la calidad del equipo Work (activity) to improve the quality of equipment. | Aktivnosti za poboljšanje kvalitete opreme | Work (activity) to improve the quality of equipment. | Lucrare (activitate) de ridicare a echipamentelor la standarde moderne. | X | X | X | X | X | X
| Updating |  | Updating | Modernizace | Updating | Mise à jour de l'appareillage | Aktualisierung | 最新化 | Oppdatering | Updating | Actualización | Moderniziranje | Updating | Modernizare (Updating) | X | X | X | X | X | X
| Work (activity) to bring equipment up to modern standards. |  | Work (activity) to bring equipment up to modern standards. | Práce na zarizeni s cilem vytvorit soulad parametru zarizeni s modernimi standardy (normami) | Work (activity) to bring equipment up to modern standards. | Activité pour équiper l'appareil de composants plus modernes. | Arbeit (Aktivität) zur Angleichung eines Gerätes auf den neuesten Stand. | 最新の標準機種を適用する作業。 | Arbeid med å bringe utstyret til moderne standarder. | Work (activity) to bring equipment up to modern standards. | Trabajos para incorporar al equipos los nuevos estandares Work (activity) to bring equipment up to modern standards. | Aktivnosti za usklađivanje opreme s najnovijim standardima | Work (activity) to bring equipment up to modern standards. | Lucrare (activitate) de ridicare a echipamentelor la standarde moderne. | X | X | X | X | X | X
| Extension |  | Extension | Rozsireni | Extension | Extension | Erweiterung | 増設 | Utvidelse | Extension | Extensión | Proširenje | Extension | Extindere | X | X | X | X | X | X
| The addition or change of power system function by the construction of, e.g. new exits after the substation has entered service. |  | The addition or change of power system function by the construction of, e.g. new exits after the substation has entered service. | Pridani nebo zmena systemovych funkcnich vlastnosti rozvodny prostrednictvim napr. dostavby novych poli do jiz existujici provozovane rozvodny | The addition or change of power system function by the construction of, e.g. new exits after the substation has entered service. | Addition de nouvelles travées disjoncteur par exemple après que le poste est été mis en service. | Das Hinzufügen oder Verändern einer Systemfunktionalität durch die Errichtung von z.B. neuen Abgängen nach der Inbetriebsetzung. | 運転中の既設変電所に、電力システム機能の変更や増強のために新しい機器を増設する作業。 | Utvidelse av systemts funksjoner ved ekempelvis å byggen en ny avgang på en stasjon etter at stasjonen har vært i drift en tid. | The addition or change of power system function by the construction of, e.g. new exits after the substation has entered service. | La incorporación o cambio de función del sistema por la contrucción de, p.e. una nueva salida después de que la subestación haya entrado en servicio. | Dodavanje ili promjene funkcija postrojenja zahvatima u konstrukciji | The addition or change of power system function by the construction of, e.g. new exits after the substation has entered service. | Adaugarea sau schimbarea functiilor unui sistem, prin construirea, de ex. a unor noi iesiri dupa ce statia a fost pusa in functiune. | X | X | X | X | X | X
[15 empty] | X | X | X | X | X | X
| capacitor element |  | capacitor element | device consisting essentially of two electrodes separated by a dielectric
| device consisting essentially of two electrodes separated by a dielectric (from IEC 60871-1) |  | device consisting essentially of two electrodes separated by a dielectric (from IEC 60871-1)
| capacitor unit |  | capacitor unit
| assembly of one or more capacitor elements in the same container with terminals brought out (from IEC 60871-1) |  | assembly of one or more capacitor elements in the same container with terminals brought out (from IEC 60871-1) | number of capacitor units connected so as to act together
| capacitor bank |  | capacitor bank | one or more capacitor banks and their accessories
| number of capacitor units connected so as to act together (from IEC 60871-1) |  | number of capacitor units connected so as to act together (from IEC 60871-1)
| capacitor installation |  | capacitor installation
| one or more capacitor banks and their accessories (from IEC 60871-1) |  | one or more capacitor banks and their accessories (from IEC 60871-1)
Surge Arrester
A protective device that is intended to limit transient overvoltages by diverting surge currents. It contains at least one nonlinear component and is returning to its original status after limiting the overvoltage.
Post Insulator
Insulator intended to give rigid support to a live part which is to be insulated form earth or from another live part. Note 1 - A post insulator may be an assembly of a number of post insulator units Note 2 - Post insulators for substations are also known as station post insulators
1
2
1
2
3a
3b
1
2
1
2
3a
3b

## DEV
Age Range
0 … 5
5 … 10
10 … 15
15 … 20
20 … 25
25 … 30
30 … 40
40 … 50
50 … 60
60 …
VERSION TRACKING
Version Number | Changes
11 | * Fixed: issue with saving * adding and linking the page PI_GI * Changes to CAP_GI made by Tommie
12 | * Definition for post insulators has been extended
13 | *Definition of the printing range
14
15